Register(s) Com.Obj. Name Dim Type Len Dec Min Max Group
============================================================================================
40001 8505 Dif Ext Imp1 kW Integer 2 0 -32768 32767 Imp inputs CU
40002 8506 Dif Ext Imp2 kW Integer 2 0 -32768 32767 Imp inputs CU
40003 8235 BIN Binary#1 2 - - - Bin inputs CU
40004 9107 BIN-1 Binary#2 1 - - - Binary Inputs
40005 9108 (N/A)
40006 9109 (N/A)
40007 9110 (N/A)
40008 9111 (N/A)
40009 9112 (N/A)
40010 9113 (N/A)
40011 9114 (N/A)
40012 8239 BOUT Binary#3 2 - - - Bin outputs CU
40013 8213 Ubat V Integer 2 1 0 360 Analog CU
40014 10124 CPU temp °C Integer 2 1 -200 800 Analog CU
40015 10603 (N/A)
40016 9155 MixRichClapPos % Integer 2 1 0 1100 Analog CU
40017 9156 T Canopy °C Integer 2 1 0 1200 Analog CU
40018 9157 Oil Temperat °C Integer 2 1 0 1300 Analog CU
40019 9158 Press Oil kPa Integer 2 1 0 9000 Analog CU
40020 9159 (N/A)
40021 9160 (N/A)
40022 9161 (N/A)
40023 9162 (N/A)
40024 9163 T P.C. In °C Integer 2 1 0 1200 AnalogInputs 1
40025 9164 T P.C. Out °C Integer 2 1 0 1200 AnalogInputs 1
40026 9165 T S.C. Gen °C Integer 2 1 0 1200 AnalogInputs 1
40027 9166 T S.C. In °C Integer 2 1 0 1200 AnalogInputs 1
40028 9167 (N/A)
40029 9168 (N/A)
40030 9169 (N/A)
40031 9170 (N/A)
40032 9171 (N/A)
40033 9172 (N/A)
40034 9173 (N/A)
40035 9174 (N/A)
40036 9175 (N/A)
40037 9176 (N/A)
40038 9177 (N/A)
40039 9178 (N/A)
40040 9179 (N/A)
40041 9180 (N/A)
40042 9181 (N/A)
40043 9182 (N/A)
40044 9183 (N/A)
40045 9184 (N/A)
40046 9185 (N/A)
40047 9186 (N/A)
40048 9187 (N/A)
40049 9188 (N/A)
40050 9189 (N/A)
40051 9190 (N/A)
40052 9191 (N/A)
40053 9192 (N/A)
40054 9193 (N/A)
40055 9194 (N/A)
40056-40103 (48) 0 (N/A)
40104 10153 Engine Speed-0 RPM Integer 2 0 0 3000 ECU
40105 10154 GlobalTiming-0 deg Integer 2 1 -2000 3019 ECU
40106 10155 Timing1-0 deg Integer 2 1 -2000 3019 ECU
40107 10156 Timing2-0 deg Integer 2 1 -2000 3019 ECU
40108 10157 Timing3-0 deg Integer 2 1 -2000 3019 ECU
40109 10158 Timing4-0 deg Integer 2 1 -2000 3019 ECU
40110 10159 Dwell time 1-0 us Integer 2 0 0 25000 ECU
40111 10160 Dwell time 2-0 us Integer 2 0 0 25000 ECU
40112 10161 Dwell time 3-0 us Integer 2 0 0 25000 ECU
40113 10162 Dwell time 4-0 us Integer 2 0 0 25000 ECU
40114 10163 Dwell optim1-0 us Integer 2 0 0 25000 ECU
40115 10164 Dwell optim2-0 us Integer 2 0 0 25000 ECU
40116 10165 Dwell optim3-0 us Integer 2 0 0 25000 ECU
40117 10166 Dwell optim4-0 us Integer 2 0 0 25000 ECU
40118 10167 Battery Volt-0 V Integer 2 1 0 300 ECU
40119 10168 Engine Speed-1 RPM Integer 2 0 0 3000 ECU
40120 10169 ECU BIN1 Binary#4 1 - - - ECU
40121 10170 ECU BIN2 Binary#5 1 - - - ECU
40122 10171 ECU BOUT1 Binary#6 1 - - - ECU
40123 10172 ECU BOUT2 Binary#7 1 - - - ECU
40124-40125 ( 2) 10173 ECU-AIN-L 1 - Integer 4 0 - - ECU
40126-40127 ( 2) 10174 ECU-AIN-L 2 - Integer 4 0 - - ECU
40128 10182 ECU StrList1 List#1 1 - 1248 1248 (No group)
40129 10183 ECU StrList2 List#2 1 - 1249 1249 (No group)
40130 9143 LogBout 1 Binary#8 2 - - - Log Bout
40131 9144 LogBout 2 Binary#9 2 - - - Log Bout
40132 9145 LogBout 3 Binary#10 2 - - - Log Bout
40133 9146 LogBout 4 Binary#11 2 - - - Log Bout
40134 9147 LogBout 5 Binary#12 2 - - - Log Bout
40135 9148 LogBout 6 Binary#13 2 - - - Log Bout
40136 9149 LogBout 7 Binary#14 2 - - - Log Bout
40137 10580 VPIO BOUT1 Binary#15 1 - - - VPIO
40138 10581 (N/A)
40139 10582 (N/A)
40140 10583 (N/A)
40141-40156 (16) 10011 (N/A)
40157 10627 RemoteControl Binary#16 2 - - - Log Bout
40158 8393 SW version Unsigned 1 1 0 255 Info
40159 8707 SW branch Unsigned 1 0 0 255 Info
40160 8480 Application Unsigned 1 0 0 255 Info
40161-40162 ( 2) 9090 PasswordDecode Unsigned 4 0 - - Info
40163 9244 Engine state List#3 1 - 1161 1182 Info
40164 9245 Breaker state List#4 1 - 1183 1195 Info
40165 9589 Breaker timer s Unsigned 2 1 0 36000 Invisible
40166-40167 ( 2) 10130 (N/A)
40168 9574 ControllerMode List#5 1 - 1156 1160 Info
40169 9887 ControllerMode List#5 1 - 1156 1160 Invisible
40170 0 (N/A)
40171 8546 CAN16 Binary 2 - - - Info
40172 8827 CAN32 Binary 2 - - - Info
40173 8449 Status Binary#17 2 - - - Invisible
40174 10040 Timer text List#6 1 - 1200 1232 Info
40175 8955 Timer val s Unsigned 2 0 0 65535 Info
40176 10226 ECU DiagSource List#7 1 - 1233 1237 Info
40177-40178 ( 2) 10232 ECU FC Unsigned 4 0 - - ECU diag
40179 10233 ECU FMI Unsigned 1 0 0 255 ECU diag
40180 10234 ECU OC Unsigned 1 0 0 255 ECU diag
40181 10424 PLC-BOUT 1 Binary#18 1 - - - PLC
40182 10425 PLC-BOUT 2 Binary#19 1 - - - PLC
40183 10426 PLC-BOUT 3 Binary#20 1 - - - PLC
40184 10427 PLC-BOUT 4 Binary#21 1 - - - PLC
40185 10428 (N/A)
40186 10429 (N/A)
40187 10430 (N/A)
40188 10431 (N/A)
40189 10432 (N/A)
40190 10433 (N/A)
40191 10434 (N/A)
40192 10435 (N/A)
40193 10436 (N/A)
40194 10437 (N/A)
40195 10438 (N/A)
40196 10439 (N/A)
40197 10360 ConsumptObjPLC kW Integer 2 1 -32768 32767 PLC
40198 10361 Igni Timing ° Integer 2 0 -32768 32767 PLC
40199 10362 Igni DwellTime us Integer 2 0 -32768 32767 PLC
40200 10363 Igni Test - Integer 2 0 -32768 32767 PLC
40201 10364 RedPWR Freq % Integer 2 0 -32768 32767 PLC
40202 10365 (N/A)
40203 10366 (N/A)
40204 10367 (N/A)
40205 10368 (N/A)
40206 10369 (N/A)
40207 10370 (N/A)
40208 10371 (N/A)
40209 10372 (N/A)
40210 10373 (N/A)
40211 10374 (N/A)
40212 10375 (N/A)
40213 10376 (N/A)
40214 10377 (N/A)
40215 10378 (N/A)
40216 10379 (N/A)
40217 10380 (N/A)
40218 10381 (N/A)
40219 10382 (N/A)
40220 10383 (N/A)
40221 10384 (N/A)
40222 10385 (N/A)
40223 10386 (N/A)
40224 10387 (N/A)
40225 10388 (N/A)
40226 10389 (N/A)
40227 10390 (N/A)
40228 10391 (N/A)
40229 10392 (N/A)
40230 10393 (N/A)
40231 10394 (N/A)
40232 10395 (N/A)
40233 10396 (N/A)
40234 10397 (N/A)
40235 10398 (N/A)
40236 10399 (N/A)
40237 10400 (N/A)
40238 10401 (N/A)
40239 10402 (N/A)
40240 10403 (N/A)
40241 10404 (N/A)
40242 10405 (N/A)
40243 10406 (N/A)
40244 10407 (N/A)
40245 10408 (N/A)
40246 10409 (N/A)
40247 10410 (N/A)
40248 10411 (N/A)
40249 10412 (N/A)
40250 10413 (N/A)
40251 10414 (N/A)
40252 10415 (N/A)
40253 10416 (N/A)
40254 10417 (N/A)
40255 10418 (N/A)
40256 10419 (N/A)
40257 10420 (N/A)
40258 10421 (N/A)
40259 10422 (N/A)
40260 10423 (N/A)
40261 10504 (N/A)
40262 10505 (N/A)
40263 10506 (N/A)
40264 10507 (N/A)
40265 10508 (N/A)
40266 10509 (N/A)
40267 10510 (N/A)
40268 10511 (N/A)
40269 10572 (N/A)
40270 10573 (N/A)
40271 10574 (N/A)
40272 10575 (N/A)
40273 10576 (N/A)
40274 10577 (N/A)
40275 10578 (N/A)
40276 10579 (N/A)
40277 10584 (N/A)
40278 10585 (N/A)
40279 10586 (N/A)
40280 10587 (N/A)
40281 8192 Gen V L1-N V Unsigned 2 0 0 8277* Gener values
40282 8193 Gen V L2-N V Unsigned 2 0 0 8277* Gener values
40283 8194 Gen V L3-N V Unsigned 2 0 0 8277* Gener values
40284 10645 Gen V V Unsigned 2 0 0 8277* Gener values
40285 9628 Gen V L1-L2 V Unsigned 2 0 0 9673* Gener values
40286 9629 Gen V L2-L3 V Unsigned 2 0 0 9673* Gener values
40287 9630 Gen V L3-L1 V Unsigned 2 0 0 9673* Gener values
40288 8210 Gen freq Hz Unsigned 2 1 400 700 Gener values
40289 9851 (N/A)
40290 8198 Gen curr L1 A Unsigned 2 0 0 8275* Gener values
40291 8199 Gen curr L2 A Unsigned 2 0 0 8275* Gener values
40292 8200 Gen curr L3 A Unsigned 2 0 0 8275* Gener values
40293 8204 Pwr factor Integer 1 2 -100 100 Gener values
40294 8395 Load char Char 1 - - - Gener values
40295 8226 (N/A)
40296 8202 Act power kW Integer 2 1 0 8276* Gener values
40297 10641 Act pwr rel % Integer 2 2 0 10000 Gener values
40298 8524 Act pwr L1 kW Integer 2 1 0 8276* Gener values
40299 8525 Act pwr L2 kW Integer 2 1 0 8276* Gener values
40300 8526 Act pwr L3 kW Integer 2 1 0 8276* Gener values
40301 8203 React power kVAr Integer 2 1 -32768 32767 Gener values
40302 10642 (N/A)
40303 8527 React pwr L1 kVAr Integer 2 1 -32768 32767 Gener values
40304 8528 React pwr L2 kVAr Integer 2 1 -32768 32767 Gener values
40305 8529 React pwr L3 kVAr Integer 2 1 -32768 32767 Gener values
40306 8565 Appar pwr kVA Integer 2 1 -32768 32767 Gener values
40307 8530 Appar pwr L1 kVA Integer 2 1 -32768 32767 Gener values
40308 8531 Appar pwr L2 kVA Integer 2 1 -32768 32767 Gener values
40309 8532 Appar pwr L3 kVA Integer 2 1 -32768 32767 Gener values
40310 8533 Pwr factor L1 Integer 1 2 -100 100 Gener values
40311 8534 Pwr factor L2 Integer 1 2 -100 100 Gener values
40312 8535 Pwr factor L3 Integer 1 2 -100 100 Gener values
40313 10548 Gen V unbal % Unsigned 2 0 0 200 Gener values
40314 10550 Gen I unbal % Unsigned 2 0 0 200 Gener values
40315 8445 WiringCheck Unsigned 2 0 0 65535 Invisible
40316 10604 (N/A)
40317 8626 Load char L1 Char 1 - - - Gener values
40318 8627 Load char L2 Char 1 - - - Gener values
40319 8628 Load char L3 Char 1 - - - Gener values
40320 8195 Mains V L1-N V Unsigned 2 0 0 9888* Mains values
40321 8196 Mains V L2-N V Unsigned 2 0 0 9888* Mains values
40322 8197 Mains V L3-N V Unsigned 2 0 0 9888* Mains values
40323 10666 Mains V V Unsigned 2 0 0 9888* Mains values
40324 9631 Mains V L1-L2 V Unsigned 2 0 0 9907* Mains values
40325 9632 Mains V L2-L3 V Unsigned 2 0 0 9907* Mains values
40326 9633 Mains V L3-L1 V Unsigned 2 0 0 9907* Mains values
40327 8208 Im3/EarthFC A Unsigned 2 0 0 8566* Mains values
40328 8211 Mains freq Hz Unsigned 2 1 400 700 Mains values
40329 10602 (N/A)
40330 8703 P mains kW Integer 2 1 -32768 32767 Mains values
40331 8704 Q mains kVAr Integer 2 1 -32768 32767 Mains values
40332 8705 Mains PF Integer 1 2 -100 100 Mains values
40333 8709 Mains LChr Char 1 - - - Mains values
40334 10549 Mains V unbal % Unsigned 2 0 0 200 Mains values
40335 8224 Slip freq Hz Integer 2 2 -10000 10000 Gener values
40336 8225 Angle ° Integer 2 1 -1800 1800 Gener values
40337-40338 ( 2) 10601 Object P kW Integer 4 1 - - Mains values
40339-40340 ( 2) 10644 Object Q kVAr Integer 4 1 - - Mains values
40341 9025 Object PF Integer 1 2 -100 100 Mains values
40342 9026 Object LChr Char 1 - - - Mains values
40343 9847 MaxVectorS ° Unsigned 2 1 0 3000 Mains values
40344 9889 Volt match 123 Binary 1 - - - Invisible
40345 9050 (N/A)
40346 8209 (N/A)
40347 10123 RPM RPM Integer 2 0 0 8253* Engine values
40348 9620 T Cyl aver °C Integer 2 0 -32768 32767 Engine values
40349 10526 T Cyl max °C Integer 2 0 -32768 32767 Engine values
40350 10527 T Cyl min °C Integer 2 0 -32768 32767 Engine values
40351 9588 Engine timer s Unsigned 2 1 0 36000 Invisible
40352 9591 StatLdShed List#8 1 - 1196 1199 Load shedding
40353 10646 (N/A)
40354 10660 (N/A)
40355 9975 (N/A)
40356 10659 (N/A)
40357 8663 ActPwrReq kW Integer 2 1 0 8276* Sync/Load ctrl
40358 10643 (N/A)
40359 10137 Speed request % Integer 2 1 0 1000 Sync/Load ctrl
40360 9052 SpdRegOut V Integer 2 3 -10000 10000 Sync/Load ctrl
40361 9053 VoltRegOut % Integer 2 1 0 1000 Volt/PF ctrl
40362 10792 SystLoadCtrl List#9 1 - 1142 1147 Sync/Load ctrl
40363 10793 SystPfCtrl List#10 1 - 1148 1151 Volt/PF ctrl
40364 10007 IE Pwr visual kW Integer 2 1 0 8276* Invisible
40365 9032 Req PF Integer 1 2 -128 127 Invisible
40366 9033 Req LChr Char 1 - - - Invisible
40367-40368 ( 2) 10656 (N/A)
40369-40370 ( 2) 10657 (N/A)
40371-40372 ( 2) 10658 (N/A)
40373 10619 (N/A)
40374-40375 ( 2) 10621 (N/A)
40376 10620 (N/A)
40377-40378 ( 2) 10622 (N/A)
40379 10796 (N/A)
40380 10797 (N/A)
40381 8624 (N/A)
40382 8625 (N/A)
40383 8622 (N/A)
40384 8623 (N/A)
40385 10788 (N/A)
40386 10786 (N/A)
40387 10787 (N/A)
40388 10012 (N/A)
40389-40390 ( 2) 10913 (N/A)
40391 9125 BOUT-1 Binary#22 1 - - - Binary Outputs
40392 9126 (N/A)
40393 9127 (N/A)
40394 9128 (N/A)
40395 9129 (N/A)
40396 9130 (N/A)
40397-40402 ( 6) 0 (N/A)
40403-40404 ( 2) 10927 NextTime1-4 Time 3 - - - Info
40405-40406 ( 2) 10928 NextTime5-8 Time 3 - - - Info
40407-40408 ( 2) 10929 NextTime9-12 Time 3 - - - Info
40409-40410 ( 2) 10930 NextTime13-16 Time 3 - - - Info
40411-40412 ( 2) 10931 NextDate1-4 Date 3 - - - Info
40413-40414 ( 2) 10932 NextDate5-8 Date 3 - - - Info
40415-40416 ( 2) 10933 NextDate9-12 Date 3 - - - Info
40417-40418 ( 2) 10934 NextDate13-16 Date 3 - - - Info
40419 9150 LogBout 8 Binary#23 2 - - - Log Bout
40420-40421 ( 2) 10998 (N/A)
40422-40423 ( 2) 10999 (N/A)
40424 11004 ExtValue1 X Integer 2 0 11012* 11016* Force value
40425 11005 ExtValue2 X Integer 2 0 11013* 11017* Force value
40426 11006 ExtValue3 X Integer 2 0 11014* 11018* Force value
40427 11007 ExtValue4 X Integer 2 0 11015* 11019* Force value
40428-40433 ( 6) 0 (N/A)
40434 11081 Reg16 Binary 2 - - - Info
40435 11082 Reg32 Binary 2 - - - Info
40436 8451 UgOverLimit V Unsigned 2 0 0 65535 Invisible
40437 8452 UgUnderLimit V Unsigned 2 0 0 65535 Invisible
40438 8453 UmOverLimit V Unsigned 2 0 0 65535 Invisible
40439 8454 UmUnderLimit V Unsigned 2 0 0 65535 Invisible
40440 10006 SpeedReq RPM RPM Unsigned 2 0 0 3000 Sync/Load ctrl
40441-40442 ( 2) 11388 StatusDW Binary#24 4 - - - Invisible
40443 11341 (N/A)
40444 11342 (N/A)
40445 11343 (N/A)
40446 11344 (N/A)
40447 11390 (N/A)
40448 11391 (N/A)
40449 11392 (N/A)
40450 11393 (N/A)
40451 10688 (N/A)
40452 10689 (N/A)
40453 10690 (N/A)
40454 10691 (N/A)
40455 10692 (N/A)
40456 10693 (N/A)
40457 10694 (N/A)
40458 10695 (N/A)
40459 10696 (N/A)
40460 10697 (N/A)
40461 10698 (N/A)
40462 10699 (N/A)
40463 10700 (N/A)
40464 10701 (N/A)
40465 10702 (N/A)
40466 10703 (N/A)
40467 10752 (N/A)
40468 10753 (N/A)
40469 10760 (N/A)
40470 10761 (N/A)
40471-40472 ( 2) 10768 (N/A)
40473-40474 ( 2) 10769 (N/A)
40475 10776 (N/A)
40476 10777 (N/A)
40477 11614 CPU temp avg °C Integer 2 1 -200 800 Statistics
40478 10090 AFS Valve pos % Integer 2 2 0 10000 AFS control
40479 13570 AFS Vlv offset % Integer 2 2 0 10000 AFS control
40480 13572 AFS Vlv reg % Integer 2 2 0 10000 AFS control
40481 10092 AFS Valve fdb % Integer 2 2 0 10000 AFS control
40482 10091 LAM required mV Integer 2 0 0 1000 AFS control
40483 10093 LAM actual mV Integer 2 0 0 1000 AFS control
40484 8222 Ext Imp1 Dec kWh Unsigned 2 0 0 65535 Imp inputs CU
40485 8223 Ext Imp2 Dec kWh Unsigned 2 0 0 65535 Imp inputs CU
40486 11670 (N/A)
40487 11671 (N/A)
40488 11672 (N/A)
40489 11673 (N/A)
40490 11674 (N/A)
40491 11834 (N/A)
40492 11833 ReqEngineSpeed RPM Integer 2 0 0 3000 Sync/Load ctrl
40493 11217 (N/A)
40494 11218 (N/A)
40495 11219 (N/A)
40496 11220 (N/A)
40497 11598 (N/A)
40498 11221 (N/A)
40499 11306 (N/A)
40500 11307 (N/A)
40501 12084 (N/A)
40502 12085 (N/A)
40503 12086 (N/A)
40504 12087 (N/A)
40505 12088 (N/A)
40506 12089 (N/A)
40507 12090 (N/A)
40508 9678 Act power kW Integer 2 1 0 8276* Invisible
40509 12641 RPM RPM Integer 2 0 0 8253* Invisible
40510 10196 GL16 Binary 2 - - - Info
40511 10197 GL32 Binary 2 - - - Info
40512-40513 ( 2) 12482 DPF status Binary 4 - - - Invisible
40514 11896 LogBout 9 Binary#25 2 - - - Log Bout
40515 13301 (N/A)
40516 13302 (N/A)
40517 13303 (N/A)
40518 13304 (N/A)
40519 13305 (N/A)
40520 13306 (N/A)
40521 13307 (N/A)
40522 13308 (N/A)
40523 13309 (N/A)
40524 13310 (N/A)
40525 13311 (N/A)
40526 13312 (N/A)
40527 13313 (N/A)
40528 13314 (N/A)
40529 13315 (N/A)
40530 13316 (N/A)
40531 13317 (N/A)
40532 13318 (N/A)
40533 13319 (N/A)
40534 13320 (N/A)
40535 13321 (N/A)
40536 13322 (N/A)
40537 13323 (N/A)
40538 13324 (N/A)
40539 13325 (N/A)
40540 13326 (N/A)
40541 13327 (N/A)
40542 13328 (N/A)
40543 13329 (N/A)
40544 13330 (N/A)
40545 13331 (N/A)
40546 13332 (N/A)
40547 13333 (N/A)
40548-40549 ( 2) 13334 (N/A)
40550-40551 ( 2) 13335 (N/A)
40552 13336 (N/A)
40553 13337 (N/A)
40554 12364 TS1 List#11 1 - 1152 1153 Invisible
40555 12365 TS2 List#11 1 - 1152 1153 Invisible
40556 12366 TS3 List#11 1 - 1152 1153 Invisible
40557 12367 TS4 List#11 1 - 1152 1153 Invisible
40558 12368 TS5 List#11 1 - 1152 1153 Invisible
40559 12369 TS6 List#12 1 - 1154 1155 Invisible
40560 12370 TS7 List#12 1 - 1154 1155 Invisible
40561-40568 ( 8) 11872 DeviceLifetime String0 16 - - - Invisible
40569 11897 LogBout 10 Binary#26 2 - - - Log Bout
40570 13617 IOT BOut Binary#27 1 - - - IO TEDOM
40571 13618 IOT command Binary#28 1 - - - IO TEDOM
40572 13619 IOT Status Binary#29 2 - - - IO TEDOM
40573 13620 T S.C. Out °C Integer 2 1 -350 2000 IO TEDOM
40574 13621 Reserve °C Integer 2 0 0 0 IO TEDOM
40575 13622 T.Cat °C Integer 2 0 0 1090 IO TEDOM
40576 13623 Reserve °C Integer 2 0 0 0 IO TEDOM
40577 13624 Lambda S mV Integer 2 0 0 1200 IO TEDOM
40578 13625 Lambda L mV Integer 2 1 0 10000 IO TEDOM
40579 13626 BuildConsumpt mA Integer 2 2 -2000 2000 IO TEDOM
40580 13627 StepperPos st Integer 2 0 0 10000 IO TEDOM
40581 8507 StartPosition % Integer 2 2 0 10000 Invisible
40582 8508 RunPosition % Integer 2 2 0 10000 Invisible
40583 8509 LoPwrPosition % Integer 2 2 0 10000 Invisible
40584 8510 MixPos 1 % Integer 2 2 0 10000 Invisible
40585 8511 MixPos 2 % Integer 2 2 0 10000 Invisible
40586 8512 MixPos 3 % Integer 2 2 0 10000 Invisible
40587 8513 MixPos 4 % Integer 2 2 0 10000 Invisible
40588 8514 MixPos 5 % Integer 2 2 0 10000 Invisible
40589 8515 LAM 1 mV Integer 2 0 1 1200 Invisible
40590 8516 LAM 2 mV Integer 2 0 1 1200 Invisible
40591 8517 LAM 3 mV Integer 2 0 1 1200 Invisible
40592 8518 LAM 4 mV Integer 2 0 1 1200 Invisible
40593 8519 LAM 5 mV Integer 2 0 1 1200 Invisible
40594 8520 Pwr 1 kW Integer 2 1 0 8276* Invisible
40595 13637 AFS Step pos st Integer 2 0 0 10000 AFS control
40596 8540 Pwr 2 kW Integer 2 1 0 8276* Invisible
40597 8541 Pwr 3 kW Integer 2 1 0 8276* Invisible
40598 8542 Pwr 4 kW Integer 2 1 0 8276* Invisible
40599 8543 Pwr 5 kW Integer 2 1 0 8276* Invisible
40600 11271 AirGate Status Unsigned 1 0 0 255 Info
43001-43008 ( 8) 8637 Gen-set name String0 16 - - - Comms settings
43009 8276 Nomin power kW Unsigned 2 1 10 1000 Basic settings
43010 8275 Nomin current A Unsigned 2 0 1 10000 Basic settings
43011 8274 CT ratio prim A Unsigned 2 0 1 15000 Basic settings
43012 10556 CT ratio sec List#13 1 - 1000 1001 Basic settings
43013 8566 Im3/ErFlCurCTp A Unsigned 2 0 1 15000 Basic settings
43014 10557 Im3/ErFlCurCTs List#13 1 - 1000 1001 Basic settings
43015 9579 VT ratio V/V Unsigned 2 2 10 50000 Basic settings
43016 10662 Vg InpRangeSel List#14 1 - 1002 1003 Basic settings
43017 9580 Vm VT ratio V/V Unsigned 2 2 10 50000 Basic settings
43018 10663 Vm InpRangeSel List#14 1 - 1002 1003 Basic settings
43019 8277 GenNomV V Unsigned 2 0 10 34641 Basic settings
43020 9673 GenNomVph-ph V Unsigned 2 0 17 60000 Basic settings
43021 9888 MainsNomV V Unsigned 2 0 10 34641 Mains protect
43022 9907 MainsNomVph-ph V Unsigned 2 0 17 60000 Mains protect
43023 10647 FixVoltProtSel List#15 1 - 1091 1092 Mains protect
43024 8278 Nominal freq Hz Unsigned 2 0 45 65 Mains protect
43025 8252 Gear teeth Unsigned 2 0 0 500 Basic settings
43026 8253 Nominal RPM RPM Unsigned 2 0 100 4000 Basic settings
43027 8315 ControllerMode List#5 1 - 1156 1160 Basic settings
43028 9983 FltRes GoToMAN List#16 1 - 1004 1005 Basic settings
43029 10588 Local buttons List#17 1 - 1006 1008 Basic settings
43030 10121 DispBaklightTO min Unsigned 1 0 0 241 Basic settings
43031 9921 CAN2emptDetect List#16 1 - 1004 1005 Comms settings
43032 9095 Starting RPM RPM Unsigned 2 0 0 1500 Engine params
43033 9681 Starting POil kPa Integer 2 1 0 10000 Engine params
43034 8394 Prestart time s Unsigned 2 0 0 3600 Engine params
43035 8780 PrelubrTime s Unsigned 2 0 0 3600 Engine params
43036 8781 PrelubrPause min Unsigned 2 0 1 3000 Engine params
43037 8256 MaxCrank time s Unsigned 1 0 10 15 Engine params
43038 8257 CrnkFail pause s Unsigned 1 0 10 60 Engine params
43039 8255 (N/A)
43040 9097 Idle time s Unsigned 2 0 0 3600 Engine params
43041 8259 Min stab time s Unsigned 2 0 1 8313* Engine params
43042 8313 Max stab time s Unsigned 2 0 8259* 3600 Engine params
43043 9243 Warming load % Integer 2 0 0 100 Engine params
43044 9258 Warming temp °C Integer 2 1 0 1200 Engine params
43045 8562 Max warm time s Unsigned 2 0 0 3600 Engine params
43046 10046 Cooling speed List#18 1 - 1085 1086 Engine params
43047 8258 Cooling time s Unsigned 2 0 0 3600 Engine params
43048 10661 Cooldown optim List#16 1 - 1004 1005 Engine params
43049 8662 AfterCoolTime s Unsigned 2 0 0 3600 Engine params
43050 9815 Stop time s Unsigned 2 0 0 240 Engine params
43051 9695 SDVentil time s Unsigned 2 0 0 60 Engine params
43052 9100 (N/A)
43053 10525 GasValveDelay s Integer 2 1 0 50 Engine params
43054 8264 Horn timeout s Unsigned 2 0 0 3601 Engine protect
43055 8263 Overspeed % Unsigned 2 0 0 200 Engine protect
43056 9622 Max+CylDifPmin °C Integer 2 0 -32000 32000 Engine protect
43057 9623 Max-CylDifPmin °C Integer 2 0 -32000 32000 Engine protect
43058 9624 Max+CylDifPnom °C Integer 2 0 -32000 32000 Engine protect
43059 9625 Max-CylDifPnom °C Integer 2 0 -32000 32000 Engine protect
43060 9626 PminCylDifEval kW Integer 2 1 0 8276* Engine protect
43061 9627 CylDifEvalDel s Unsigned 2 0 0 600 Engine protect
43062 8638 Load ctrl PtM List#19 1 - 1065 1069 ProcessControl
43063 10120 PF ctrl PtM List#20 1 - 1070 1073 ProcessControl
43064 10599 I/E-Pm meas List#21 1 - 1074 1076 ProcessControl
43065 10598 I/E-Qm meas List#21 1 - 1074 1076 ProcessControl
43066 9046 Derating1 strt °C Integer 2 1 0 1200 ProcessControl
43067 9047 Derating1 end °C Integer 2 1 0 1200 ProcessControl
43068 9048 Derating1 pwr % Unsigned 2 0 0 100 ProcessControl
43069 10189 Derating2 strt x Integer 2 0 -32000 12439* ProcessControl
43070 10190 Derating2 end x Integer 2 0 12439* 32000 ProcessControl
43071 10191 Derating2 pwr % Unsigned 2 0 0 12440* ProcessControl
43072 8639 Base load kW Integer 2 1 0 8276* ProcessControl
43073 8640 Base PF Integer 2 2 60 120 ProcessControl
43074 8641 Import load kW Integer 2 1 -32000 32000 ProcessControl
43075 8642 Import PF Integer 2 2 60 120 ProcessControl
43076 8643 PeakLevelStart kW Integer 2 1 8644* 32000 ProcessControl
43077 8644 PeakLevelStop kW Integer 2 1 0 8643* ProcessControl
43078 9989 PeakAutS/S del s Unsigned 2 0 0 3200 ProcessControl
43079 9592 Export limit List#16 1 - 1004 1005 ProcessControl
43080 9607 TempByPwr Treq °C Integer 2 0 -32000 32000 ProcessControl
43081 9608 TempByPwr gain % Unsigned 2 2 0 10000 ProcessControl
43082 9609 TempByPwr int % Unsigned 2 1 0 1000 ProcessControl
43083 9619 Overheat prot List#16 1 - 1004 1005 ProcessControl
43084 9236 Island enable List#22 1 - 1077 1078 ProcessControl
43085 9237 ParallelEnable List#22 1 - 1077 1078 ProcessControl
43086 9235 Synchro enable List#23 1 - 1079 1082 ProcessControl
43087 9238 MFStart enable List#22 1 - 1077 1078 ProcessControl
43088 10118 (N/A)
43089 10339 (N/A)
43090 8280 OverldStrtEval % Unsigned 2 0 100 200 Gener protect
43091 8281 2POvrldStEvDel s Unsigned 2 1 0 6000 Gener protect
43092 9241 Min power PtM % Unsigned 2 0 0 100 Gener protect
43093 8282 Ishort % Unsigned 2 0 100 500 Gener protect
43094 9991 Ishort del s Unsigned 2 2 0 1000 Gener protect
43095 8283 2Inom del s Unsigned 2 1 0 6000 Gener protect
43096 8291 Gen >V BOC % Unsigned 2 0 8293* 150 Gener protect
43097 10013 Gen >V Sd % Unsigned 2 0 50 150 Gener protect
43098 8293 Gen <V BOC % Unsigned 2 0 20 8291* Gener protect
43099 9103 Gen V del s Unsigned 2 2 0 60000 Gener protect
43100 10558 (N/A)
43101 8296 Gen >f % Unsigned 2 1 8298* 1500 Gener protect
43102 8298 Gen <f % Unsigned 2 1 200 8296* Gener protect
43103 8297 Gen f del s Unsigned 2 2 0 60000 Gener protect
43104 8305 Mains >V 1.lev % Unsigned 2 0 100 150 Mains protect
43105 8307 Mains <V 1.lev % Unsigned 2 0 20 100 Mains protect
43106 8306 Mains >V 1.del s Unsigned 2 2 0 60000 Mains protect
43107 8308 Mains <V 1.del s Unsigned 2 2 0 60000 Mains protect
43108 8310 Mains >f 1.lev % Unsigned 2 1 1000 1500 Mains protect
43109 8312 Mains <f 1.lev % Unsigned 2 1 200 1000 Mains protect
43110 8311 Mains >f 1.del s Unsigned 2 2 0 60000 Mains protect
43111 9843 VectorS limit ° Unsigned 2 0 1 45 Mains protect
43112 10551 VectorS prot List#24 1 - 1093 1095 Mains protect
43113 10552 VectorS CB sel List#25 1 - 1096 1097 Mains protect
43114 11345 Mains >V 2.lev % Unsigned 2 0 100 150 Mains protect
43115 11346 Mains <V 2.lev % Unsigned 2 0 20 100 Mains protect
43116 11347 Mains >V 2.del s Unsigned 2 2 0 60000 Mains protect
43117 11348 Mains <V 2.del s Unsigned 2 2 0 60000 Mains protect
43118 11349 Mains >f 2.lev % Unsigned 2 1 1000 1500 Mains protect
43119 11350 Mains <f 2.lev % Unsigned 2 1 200 1000 Mains protect
43120 11351 Mains <f 1.del s Unsigned 2 2 0 60000 Mains protect
43121 11352 Mains >f 2.del s Unsigned 2 2 0 60000 Mains protect
43122 11353 Mains <f 2.del s Unsigned 2 2 0 60000 Mains protect
43123 8446 Mains V unbal % Unsigned 2 0 0 200 Mains protect
43124 8447 Mains Vunb del s Unsigned 2 1 0 6000 Mains protect
43125 8301 EmergStart del s Unsigned 2 0 0 600 AMF settings
43126 8303 FwRet break s Unsigned 2 1 0 600 AMF settings
43127 8389 MCB close del s Unsigned 2 1 0 600 AMF settings
43128 8302 Mains ret del s Unsigned 2 0 0 3600 AMF settings
43129 9850 MCB opens on List#26 1 - 1098 1099 AMF settings
43130 9862 ReturnWithIntr List#16 1 - 1004 1005 AMF settings
43131 8661 BreakerOverlap s Unsigned 2 1 0 3000 AMF settings
43132 8618 ReturnTo mains List#16 1 - 1004 1005 AMF settings
43133 9590 RetFromIsland List#27 1 - 1100 1101 AMF settings
43134 9054 SpeedRegChar List#28 1 - 1102 1103 Sync/Load ctrl
43135 8650 Voltage window % Unsigned 2 1 0 1000 Sync/Load ctrl
43136 9578 GtoM AngleReq ° Integer 2 0 -45 45 Sync/Load ctrl
43137 8652 Phase window ° Unsigned 2 0 0 90 Sync/Load ctrl
43138 8653 Dwell time s Unsigned 2 1 0 250 Sync/Load ctrl
43139 8715 Freq gain % Integer 2 1 0 2000 Sync/Load ctrl
43140 8716 Freq int % Integer 2 0 0 100 Sync/Load ctrl
43141 9891 Freq reg loop List#29 1 - 1104 1105 Sync/Load ctrl
43142 8718 Angle gain % Integer 2 1 0 2000 Sync/Load ctrl
43143 8656 Speed gov bias V Integer 2 2 10115* 10559* Sync/Load ctrl
43144 10115 SpeedGovLowLim V Integer 2 2 -1000 10559* Sync/Load ctrl
43145 10559 SpeedGovHiLim V Integer 2 2 10115* 1000 Sync/Load ctrl
43146 8658 Load ramp s Unsigned 2 0 0 8548* Sync/Load ctrl
43147 8659 Load gain % Integer 2 1 0 2000 Sync/Load ctrl
43148 8713 Load int % Integer 2 0 0 100 Sync/Load ctrl
43149 8547 GCB open level % Unsigned 2 0 0 100 Sync/Load ctrl
43150 8548 GCB open del s Unsigned 2 0 8658* 1800 Sync/Load ctrl
43151 8657 Sync timeout s Unsigned 2 0 1 1801 Sync/Load ctrl
43152 8725 (N/A)
43153 9035 (N/A)
43154 10784 TauSpeedActuat s Unsigned 2 1 10 3000 Sync/Load ctrl
43155 10912 RampStartLevel % Unsigned 1 0 0 100 Sync/Load ctrl
43156 10911 SpdGovPWM rate Hz Unsigned 2 0 500 3000 Sync/Load ctrl
43157 9055 AVRRegChar List#28 1 - 1102 1103 Volt/PF ctrl
43158 8501 Voltage gain % Integer 2 1 0 2000 Volt/PF ctrl
43159 8720 Voltage int % Integer 2 0 0 100 Volt/PF ctrl
43160 8503 PF gain % Integer 2 1 0 2000 Volt/PF ctrl
43161 8721 PF int % Integer 2 0 0 100 Volt/PF ctrl
43162 8500 AVR DCout bias % Integer 2 1 0 1000 Volt/PF ctrl
43163 8777 (N/A)
43164 9036 (N/A)
43165 10785 TauVoltActuat s Unsigned 2 1 10 3000 Volt/PF ctrl
43166 9649 AutoLd recon List#16 1 - 1004 1005 Load shedding
43167 8893 Ld recon delay s Unsigned 2 0 0 600 Load shedding
43168 8884 Ld shed level % Integer 2 0 8890* 200 Load shedding
43169 8887 Ld shed delay s Unsigned 2 1 0 6000 Load shedding
43170 8890 Ld recon level % Integer 2 0 0 8884* Load shedding
43171 9594 AcallCH1-Type List#30 1 - 1112 1120 Act. calls/SMS
43172 9595 AcallCH2-Type List#30 1 - 1112 1120 Act. calls/SMS
43173 9596 AcallCH3-Type List#30 1 - 1112 1120 Act. calls/SMS
43174-43189 (16) 9597 AcallCH1-Addr String0 32 - - - Act. calls/SMS
43190-43205 (16) 9598 AcallCH2-Addr String0 32 - - - Act. calls/SMS
43206-43221 (16) 9599 AcallCH3-Addr String0 32 - - - Act. calls/SMS
43222 8482 Warning List#16 1 - 1004 1005 Act. calls/SMS
43223 8484 Shutdown List#16 1 - 1004 1005 Act. calls/SMS
43224 8485 Slow stop List#16 1 - 1004 1005 Act. calls/SMS
43225 8483 Off load List#16 1 - 1004 1005 Act. calls/SMS
43226 10117 Mains protect List#16 1 - 1004 1005 Act. calls/SMS
43227 10566 BrkOpen&CoolDn List#16 1 - 1004 1005 Act. calls/SMS
43228 10567 Alarm only List#16 1 - 1004 1005 Act. calls/SMS
43229 10568 History record List#16 1 - 1004 1005 Act. calls/SMS
43230 10353 ECU Diag List#16 1 - 1004 1005 Comms settings
43231 10623 Bin selector 1 List#31 1 - 1089 1090 Engine params
43232 10624 Bin selector 2 List#31 1 - 1089 1090 Engine params
43233 10625 Bin selector 3 List#31 1 - 1089 1090 Engine params
43234 10626 Bin selector 4 List#31 1 - 1089 1090 Engine params
43235 10665 ResetActAlarms List#16 1 - 1004 1005 Engine protect
43236-43237 ( 2) 10667 Parallel Off Integer 4 0 - - Force value
43238-43239 ( 2) 10668 Force value 2 Integer 4 0 - - Force value
43240-43241 ( 2) 10669 Island Enabled Integer 4 0 - - Force value
43242-43243 ( 2) 10670 Force value 4 Integer 4 0 - - Force value
43244-43245 ( 2) 10671 Force value 5 Integer 4 0 - - Force value
43246-43247 ( 2) 10672 Force value 6 Integer 4 0 - - Force value
43248-43249 ( 2) 10673 Force value 7 Integer 4 0 - - Force value
43250-43251 ( 2) 10674 Force value 8 Integer 4 0 - - Force value
43252-43253 ( 2) 10675 Force value 9 Integer 4 0 - - Force value
43254-43255 ( 2) 10676 Force value 10 Integer 4 0 - - Force value
43256-43257 ( 2) 10677 Force value 11 Integer 4 0 - - Force value
43258-43259 ( 2) 10678 Force value 12 Integer 4 0 - - Force value
43260-43261 ( 2) 10679 Force value 13 Integer 4 0 - - Force value
43262-43263 ( 2) 10680 Force value 14 Integer 4 0 - - Force value
43264-43265 ( 2) 10681 Force value 15 Integer 4 0 - - Force value
43266-43267 ( 2) 10682 Force value 16 Integer 4 0 - - Force value
43268 10125 (N/A)
43269 10126 (N/A)
43270 10127 (N/A)
43271 10128 (N/A)
43272 10134 (N/A)
43273 10569 ForceBlock1Del s Unsigned 2 1 0 600 Engine protect
43274 10570 ForceBlock2Del s Unsigned 2 1 0 600 Engine protect
43275 10571 ForceBlock3Del s Unsigned 2 1 0 600 Engine protect
43276 10023 RunOnlyBlkDel1 s Unsigned 2 1 0 30000 Engine protect
43277 10024 RunOnlyBlkDel2 s Unsigned 2 1 0 30000 Engine protect
43278 10025 RunOnlyBlkDel3 s Unsigned 2 1 0 30000 Engine protect
43279 10131 BinInp delay 1 s Unsigned 2 1 0 6000 Engine protect
43280 10132 BinInp delay 2 s Unsigned 2 1 0 6000 Engine protect
43281 10133 BinInp delay 3 s Unsigned 2 1 0 6000 Engine protect
43282 9259 T Air Engi Yel °C Integer 2 1 0 1200 Analog protect
43283 9262 T Air Engi Red °C Integer 2 1 0 1200 Analog protect
43284 9265 Oil Temper Yel °C Integer 2 1 0 1300 Analog protect
43285 9268 T P.C. Out Yel °C Integer 2 1 0 1200 Analog protect
43286 9271 T P.C. Out Red °C Integer 2 1 0 1200 Analog protect
43287 9274 T S.C. In Yel °C Integer 2 1 0 1200 Analog protect
43288 9277 T S.C. In Red °C Integer 2 1 0 1200 Analog protect
43289 9280 TempBefore Yel °C Integer 2 1 0 1200 Analog protect
43290 9283 RedPWR Fre Yel % Integer 2 0 0 100 Analog protect
43291 9286 T S.C. Out Yel °C Integer 2 1 -350 2000 Analog protect
43292 9289 Batt >V V Integer 2 1 80 400 Analog protect
43293 9292 Batt <V V Integer 2 1 80 400 Analog protect
43294 9295 (N/A)
43295 9298 Gen V unbal % Integer 2 0 0 200 Gener protect
43296 9301 Gen I unbal % Integer 2 0 0 200 Gener protect
43297 9304 T S.C. Out Red °C Integer 2 1 -350 2000 Analog protect
43298 9307 T.Cat Yel °C Integer 2 0 0 1090 Analog protect
43299 9310 T.Cat Red °C Integer 2 0 0 1090 Analog protect
43300 9313 (N/A)
43301 9316 Lubr press Yel kPa Integer 2 1 0 9000 Analog protect
43302 9319 Lubr press Red kPa Integer 2 1 0 9000 Analog protect
43303 9322 T P.C. In Yel °C Integer 2 1 0 1200 Analog protect
43304 9325 T P.C. In Red °C Integer 2 1 0 1200 Analog protect
43305 9328 (N/A)
43306 9331 (N/A)
43307 9334 (N/A)
43308 9337 (N/A)
43309 9340 (N/A)
43310 9343 (N/A)
43311 9346 (N/A)
43312 9349 (N/A)
43313 9352 (N/A)
43314 9355 (N/A)
43315 9358 (N/A)
43316 9361 (N/A)
43317 9364 (N/A)
43318 9367 (N/A)
43319 9370 (N/A)
43320 9373 (N/A)
43321 9376 (N/A)
43322 9379 (N/A)
43323 9382 (N/A)
43324 9385 (N/A)
43325 9388 (N/A)
43326 9391 (N/A)
43327 9394 (N/A)
43328 9397 (N/A)
43329 9400 (N/A)
43330 9403 (N/A)
43331 9406 (N/A)
43332 9409 (N/A)
43333 9412 (N/A)
43334 9415 (N/A)
43335 9418 (N/A)
43336 9421 (N/A)
43337 9424 (N/A)
43338 9427 (N/A)
43339 9430 (N/A)
43340 9433 (N/A)
43341 9436 (N/A)
43342 9439 (N/A)
43343 9442 (N/A)
43344 9445 (N/A)
43345 9448 (N/A)
43346 9451 (N/A)
43347 9454 (N/A)
43348 9457 (N/A)
43349 9460 (N/A)
43350 9463 (N/A)
43351 9466 (N/A)
43352 9469 (N/A)
43353 9472 (N/A)
43354 9475 (N/A)
43355 9478 (N/A)
43356 9481 (N/A)
43357 9484 (N/A)
43358 9487 (N/A)
43359 9490 (N/A)
43360 9493 (N/A)
43361 9496 (N/A)
43362 9260 (N/A)
43363 9263 (N/A)
43364 9266 (N/A)
43365 9269 (N/A)
43366 9272 (N/A)
43367 9275 (N/A)
43368 9278 (N/A)
43369 9281 (N/A)
43370 9284 (N/A)
43371 9287 (N/A)
43372 9290 (N/A)
43373 9293 (N/A)
43374 9296 (N/A)
43375 9299 (N/A)
43376 9302 (N/A)
43377 9305 (N/A)
43378 9308 (N/A)
43379 9311 (N/A)
43380 9314 (N/A)
43381 9317 (N/A)
43382 9320 (N/A)
43383 9323 (N/A)
43384 9326 (N/A)
43385 9329 (N/A)
43386 9332 (N/A)
43387 9335 (N/A)
43388 9338 (N/A)
43389 9341 (N/A)
43390 9344 (N/A)
43391 9347 (N/A)
43392 9350 (N/A)
43393 9353 (N/A)
43394 9356 (N/A)
43395 9359 (N/A)
43396 9362 (N/A)
43397 9365 (N/A)
43398 9368 (N/A)
43399 9371 (N/A)
43400 9374 (N/A)
43401 9377 (N/A)
43402 9380 (N/A)
43403 9383 (N/A)
43404 9386 (N/A)
43405 9389 (N/A)
43406 9392 (N/A)
43407 9395 (N/A)
43408 9398 (N/A)
43409 9401 (N/A)
43410 9404 (N/A)
43411 9407 (N/A)
43412 9410 (N/A)
43413 9413 (N/A)
43414 9416 (N/A)
43415 9419 (N/A)
43416 9422 (N/A)
43417 9425 (N/A)
43418 9428 (N/A)
43419 9431 (N/A)
43420 9434 (N/A)
43421 9437 (N/A)
43422 9440 (N/A)
43423 9443 (N/A)
43424 9446 (N/A)
43425 9449 (N/A)
43426 9452 (N/A)
43427 9455 (N/A)
43428 9458 (N/A)
43429 9461 (N/A)
43430 9464 (N/A)
43431 9467 (N/A)
43432 9470 (N/A)
43433 9473 (N/A)
43434 9476 (N/A)
43435 9479 (N/A)
43436 9482 (N/A)
43437 9485 (N/A)
43438 9488 (N/A)
43439 9491 (N/A)
43440 9494 (N/A)
43441 9497 (N/A)
43442 9261 T Air Engi Del s Unsigned 2 1 0 6000 Analog protect
43443 9264 Oil Temper Del s Unsigned 2 1 0 6000 Analog protect
43444 9267 T P.C. Out Del s Unsigned 2 1 0 6000 Analog protect
43445 9270 T S.C. In Del s Unsigned 2 1 0 6000 Analog protect
43446 9273 TempBefore Del s Unsigned 2 1 0 6000 Analog protect
43447 9276 Batt volt del s Unsigned 2 1 0 6000 Analog protect
43448 9279 RedPWR Fre Del s Unsigned 2 1 0 6000 Analog protect
43449 9282 Gen V unb del s Unsigned 2 1 0 6000 Gener protect
43450 9285 Gen I unb del s Unsigned 2 1 0 6000 Gener protect
43451 9288 T S.C. Out Del s Unsigned 2 1 0 6000 Analog protect
43452 9291 T.Cat Del s Unsigned 2 1 0 6000 Analog protect
43453 9294 Lubr press Del s Unsigned 2 1 0 6000 Analog protect
43454 9297 T P.C. In Del s Unsigned 2 1 0 6000 Analog protect
43455 9300 (N/A)
43456 9303 (N/A)
43457 9306 (N/A)
43458 9309 (N/A)
43459 9312 (N/A)
43460 9315 (N/A)
43461 9318 (N/A)
43462 9321 (N/A)
43463 9324 (N/A)
43464 9327 (N/A)
43465 9330 (N/A)
43466 9333 (N/A)
43467 9336 (N/A)
43468 9339 (N/A)
43469 9342 (N/A)
43470 9345 (N/A)
43471 9348 (N/A)
43472 9351 (N/A)
43473 9354 (N/A)
43474 9357 (N/A)
43475 9360 (N/A)
43476 9363 (N/A)
43477 9366 (N/A)
43478 9369 (N/A)
43479 9372 (N/A)
43480 9375 (N/A)
43481 9378 (N/A)
43482 9381 (N/A)
43483 9384 (N/A)
43484 9387 (N/A)
43485 9390 (N/A)
43486 9393 (N/A)
43487 9396 (N/A)
43488 9399 (N/A)
43489 9402 (N/A)
43490 9405 (N/A)
43491 9408 (N/A)
43492 9411 (N/A)
43493 9414 (N/A)
43494 9417 (N/A)
43495 9420 (N/A)
43496 9423 (N/A)
43497 9426 (N/A)
43498 9429 (N/A)
43499 9432 (N/A)
43500 9435 (N/A)
43501 9438 (N/A)
43502 9441 (N/A)
43503 9444 (N/A)
43504 9447 (N/A)
43505 9450 (N/A)
43506 9453 (N/A)
43507 9456 (N/A)
43508 9459 (N/A)
43509 9462 (N/A)
43510 9465 (N/A)
43511 9468 (N/A)
43512 9471 (N/A)
43513 9474 (N/A)
43514 9477 (N/A)
43515 9480 (N/A)
43516 9483 (N/A)
43517 9486 (N/A)
43518 9489 (N/A)
43519 9492 (N/A)
43520 9495 (N/A)
43521 9498 (N/A)
43522 10440 MFprotec 0/1 Integer 2 0 0 1 PLC
43523 10441 MFprot 0/1 del s Integer 2 1 0 32767 PLC
43524 10442 Auto FR del s Integer 2 1 0 32767 PLC
43525 10443 ConsumptObjLow kW Integer 2 1 -32768 32767 PLC
43526 10444 ConsumptObjHig kW Integer 2 1 -32768 32767 PLC
43527 10445 PumpsManual0/1 Integer 2 0 -32768 32767 PLC
43528 10446 PumpsManTime s Integer 2 1 -32768 32767 PLC
43529 10447 ClapManual0/1 Integer 2 0 -32768 32767 PLC
43530 10448 Clap ManTime s Integer 2 1 -32768 32767 PLC
43531 10449 Igni Timing ° Integer 2 0 -20 20 PLC
43532 10450 Igni DwellTime us Integer 2 0 -10000 10000 PLC
43533 10451 Igni Test Integer 2 0 0 5 PLC
43534 10452 (N/A)
43535 10453 (N/A)
43536 10454 (N/A)
43537 10455 (N/A)
43538 10456 (N/A)
43539 10457 (N/A)
43540 10458 (N/A)
43541 10459 (N/A)
43542 10460 (N/A)
43543 10461 (N/A)
43544 10462 (N/A)
43545 10463 (N/A)
43546 10464 (N/A)
43547 10465 (N/A)
43548 10466 (N/A)
43549 10467 (N/A)
43550 10468 (N/A)
43551 10469 (N/A)
43552 10470 (N/A)
43553 10471 (N/A)
43554 10472 (N/A)
43555 10473 (N/A)
43556 10474 (N/A)
43557 10475 (N/A)
43558 10476 (N/A)
43559 10477 (N/A)
43560 10478 (N/A)
43561 10479 (N/A)
43562 10480 (N/A)
43563 10481 (N/A)
43564 10482 (N/A)
43565 10483 (N/A)
43566 10484 (N/A)
43567 10485 (N/A)
43568 10486 (N/A)
43569 10487 (N/A)
43570 10488 (N/A)
43571 10489 (N/A)
43572 10490 (N/A)
43573 10491 (N/A)
43574 10492 (N/A)
43575 10493 (N/A)
43576 10494 (N/A)
43577 10495 (N/A)
43578 10496 (N/A)
43579 10497 (N/A)
43580 10498 (N/A)
43581 10499 (N/A)
43582 10500 (N/A)
43583 10501 (N/A)
43584 10502 (N/A)
43585 10503 (N/A)
43586 10532 Time stamp act List#32 1 - 1121 1123 Date/Time
43587 8979 Time stamp per min Unsigned 1 0 1 240 Date/Time
43588 8551 (N/A)
43589 8488 (N/A)
43590 10592 (N/A)
43591-43592 ( 2) 10600 (N/A)
43593 10589 (N/A)
43594 10590 (N/A)
43595 10591 (N/A)
43596 10901 (N/A)
43597 9242 (N/A)
43598-43599 ( 2) 8206 Run hours h Integer 4 0 - - Statistics
43600 8207 Num starts Unsigned 2 0 0 65535 Statistics
43601 10149 NumUnscStarts Unsigned 2 0 0 65535 Statistics
43602 10528 Service time 1 h Unsigned 2 0 0 65535 Statistics
43603 10529 Service time 2 h Unsigned 2 0 0 65535 Statistics
43604 10530 Service time 3 h Unsigned 2 0 0 65535 Statistics
43605 10531 ServiceTimeSd h Unsigned 2 0 0 65535 Statistics
43606-43607 ( 2) 8205 kWhours Integer 4 0 - - Statistics
43608-43609 ( 2) 8539 kVArhours Integer 4 0 - - Statistics
43610 10122 (N/A)
43611 9099 (N/A)
43612 8727 (N/A)
43613 8774 (N/A)
43614 8779 (N/A)
43615 8775 (N/A)
43616 8776 (N/A)
43617 9890 #Neutral cont List#33 1 - 1083 1084 ProcessControl
43618 9874 (N/A)
43619 10593 (N/A)
43620 8549 (N/A)
43621 8550 (N/A)
43622 8489 (N/A)
43623 8490 (N/A)
43624 8831 (N/A)
43625 8832 (N/A)
43626 8491 (N/A)
43627 8633 (N/A)
43628 8833 (N/A)
43629 8834 (N/A)
43630 10648 (N/A)
43631 10649 (N/A)
43632 10650 (N/A)
43633 10651 (N/A)
43634 10652 (N/A)
43635 10653 (N/A)
43636 10654 (N/A)
43637 10655 (N/A)
43638 8492 (N/A)
43639 8493 (N/A)
43640 8494 (N/A)
43641 8495 (N/A)
43642 9584 (N/A)
43643 9585 (N/A)
43644 9586 (N/A)
43645 9919 (N/A)
43646 10594 (N/A)
43647 10595 (N/A)
43648 10596 (N/A)
43649 10597 (N/A)
43650 8896 (N/A)
43651 11000 CoolDnAfterBOC List#34 1 - 1087 1088 Engine params
43652 11001 Ld shed active List#35 1 - 1106 1109 Load shedding
43653 11002 DispBklStrtOff List#16 1 - 1004 1005 Basic settings
43654 11003 (N/A)
43655 11008 ExtValue1deflt X Integer 2 0 11012* 11016* Force value
43656 11009 ExtValue2deflt X Integer 2 0 11013* 11017* Force value
43657 11010 ExtValue3deflt X Integer 2 0 11014* 11018* Force value
43658 11011 ExtValue4deflt X Integer 2 0 11015* 11019* Force value
43659 11012 ExtValue1LoLim X Integer 2 0 -32000 11016* Force value
43660 11013 ExtValue2LoLim X Integer 2 0 -32000 11017* Force value
43661 11014 ExtValue3LoLim X Integer 2 0 -32000 11018* Force value
43662 11015 ExtValue4LoLim X Integer 2 0 -32000 11019* Force value
43663 11016 ExtValue1HiLim X Integer 2 0 11012* 32000 Force value
43664 11017 ExtValue2HiLim X Integer 2 0 11013* 32000 Force value
43665 11018 ExtValue3HiLim X Integer 2 0 11014* 32000 Force value
43666 11019 ExtValue4HiLim X Integer 2 0 11015* 32000 Force value
43667 11020 ExtValue1 rate X/s Integer 2 0 1 10000 Force value
43668 11021 ExtValue2 rate X/s Integer 2 0 1 10000 Force value
43669 11022 ExtValue3 rate X/s Integer 2 0 1 10000 Force value
43670 11023 ExtValue4 rate X/s Integer 2 0 1 10000 Force value
43671 11024 SHxOcol Detect List#16 1 - 1004 1005 Comms settings
43672-43675 ( 4) 10969 TimerChannel 1 Timer-L#36 8 - 1124 1131 Timer settings
43676-43679 ( 4) 10970 TimerChannel 2 Timer-L#36 8 - 1124 1131 Timer settings
43680-43683 ( 4) 10971 TimerChannel 3 Timer-L#36 8 - 1124 1131 Timer settings
43684-43687 ( 4) 10973 TimerChannel 4 Timer-L#36 8 - 1124 1131 Timer settings
43688-43691 ( 4) 10974 TimerChannel 5 Timer-L#36 8 - 1124 1131 Timer settings
43692-43695 ( 4) 10975 TimerChannel 6 Timer-L#36 8 - 1124 1131 Timer settings
43696-43699 ( 4) 10976 TimerChannel 7 Timer-L#36 8 - 1124 1131 Timer settings
43700-43703 ( 4) 10977 TimerChannel 8 Timer-L#36 8 - 1124 1131 Timer settings
43704-43707 ( 4) 10978 TimerChannel 9 Timer-L#36 8 - 1124 1131 Timer settings
43708-43711 ( 4) 10979 TimerChannel10 Timer-L#36 8 - 1124 1131 Timer settings
43712-43715 ( 4) 10980 TimerChannel11 Timer-L#36 8 - 1124 1131 Timer settings
43716-43719 ( 4) 10981 TimerChannel12 Timer-L#36 8 - 1124 1131 Timer settings
43720-43723 ( 4) 10982 TimerChannel13 Timer-L#36 8 - 1124 1131 Timer settings
43724-43727 ( 4) 10983 TimerChannel14 Timer-L#36 8 - 1124 1131 Timer settings
43728-43731 ( 4) 10984 TimerChannel15 Timer-L#36 8 - 1124 1131 Timer settings
43732-43735 ( 4) 10985 TimerChannel16 Timer-L#36 8 - 1124 1131 Timer settings
43736 10994 ConvCoefPulse1 /X Unsigned 2 0 1 65000 Basic settings
43737 10995 ConvCoefPulse2 /X Unsigned 2 0 1 65000 Basic settings
43738 10996 ConvCoefPulse3 /X Unsigned 2 0 1 65000 Basic settings
43739 10997 ConvCoefPulse4 /X Unsigned 2 0 1 65000 Basic settings
43740-43741 ( 2) 10986 NumStarterAct Unsigned 4 0 - - Statistics
43742-43743 ( 2) 10987 PulseCounter 2 Unsigned 4 0 - - Statistics
43744-43745 ( 2) 10988 PulseCounter 3 Unsigned 4 0 - - Statistics
43746-43747 ( 2) 10989 PulseCounter 4 Unsigned 4 0 - - Statistics
43748-43749 ( 2) 10990 (N/A)
43750-43751 ( 2) 10991 (N/A)
43752-43753 ( 2) 10992 (N/A)
43754-43755 ( 2) 10993 (N/A)
43756 9906 (N/A)
43757 8486 Reverse power % Unsigned 1 0 0 50 Gener protect
43758 8552 ReversePwr del s Unsigned 2 1 0 6000 Gener protect
43759 11327 LB/UART Log List#16 1 - 1004 1005 Comms settings
43760 10560 TotalDownTime h Unsigned 2 0 0 65535 Statistics
43761 10564 DnTimeReqToRun h Unsigned 2 0 0 65535 Statistics
43762 11386 (N/A)
43763 11387 (N/A)
43764 10795 (N/A)
43765 11394 Acall+SMS lang Unsigned 1 0 1 7 Act. calls/SMS
43766 11413 ShutdownOvr List#16 1 - 1004 1005 Act. calls/SMS
43767-43768 ( 2) 11612 (N/A)
43769-43770 ( 2) 11613 (N/A)
43771 9643 (N/A)
43772-43773 ( 2) 8536 Day kWhours Integer 4 0 - - Statistics
43774 11036 kWh pulse kWh Unsigned 2 0 0 65535 Basic settings
43775-43776 ( 2) 11035 (N/A)
43777 10063 StartPositionA % Unsigned 2 2 0 10000 AFS control
43778 10065 RunPositionA % Unsigned 2 2 0 10000 AFS control
43779 10067 LoPwrPositionA % Unsigned 2 2 0 10000 AFS control
43780 8420 LAM power 1A kW Integer 2 1 0 8421* AFS control
43781 8421 LAM power 2A kW Integer 2 1 8420* 8422* AFS control
43782 8422 LAM power 3A kW Integer 2 1 8421* 8423* AFS control
43783 8423 LAM power 4A kW Integer 2 1 8422* 8424* AFS control
43784 8424 LAM power 5A kW Integer 2 1 8423* 32000 AFS control
43785 8432 LAM 1A mV Integer 2 0 1 1200 AFS control
43786 8433 LAM 2A mV Integer 2 0 1 1200 AFS control
43787 8434 LAM 3A mV Integer 2 0 0 1200 AFS control
43788 8435 LAM 4A mV Integer 2 0 0 1200 AFS control
43789 8436 LAM 5A mV Integer 2 0 0 1200 AFS control
43790 8408 MixPos 1A % Integer 2 2 0 10000 AFS control
43791 8409 MixPos 2A % Integer 2 2 0 10000 AFS control
43792 8410 MixPos 3A % Integer 2 2 0 10000 AFS control
43793 8411 MixPos 4A % Integer 2 2 0 10000 AFS control
43794 8412 MixPos 5A % Integer 2 2 0 10000 AFS control
43795 10079 AFSValve MODE List#37 1 - 1134 1135 AFS control
43796 10080 MixerPosMan % Unsigned 2 2 0 10000 AFS control
43797 10876 AFSValve gain % Integer 2 1 -5000 5000 AFS control
43798 10082 AFSValve int % Unsigned 2 0 0 500 AFS control
43799 10083 AFSValve der % Unsigned 2 0 0 500 AFS control
43800 10088 LAMDeadBand mV Unsigned 2 0 0 1000 AFS control
43801 10204 GasVTest List#38 1 - 1132 1133 AFS control
43802 10205 GasVTest del s Unsigned 2 0 0 300 AFS control
43803 13571 LambdaLimPos % Integer 2 2 0 10000 AFS control
43804 11033 StartOverspeed % Unsigned 2 0 0 200 Engine protect
43805-43806 ( 2) 9040 Ext Imp 1 kWh Unsigned 4 0 - - Imp inputs CU
43807 9041 (N/A)
43808-43809 ( 2) 9817 Ext Imp 2 kWh Unsigned 4 0 - - Imp inputs CU
43810 9818 (N/A)
43811 10222 Imp Cons1 Imp Unsigned 2 3 1 65000 Imp inputs CU
43812 10223 Imp Cons2 Imp Unsigned 2 3 1 65000 Imp inputs CU
43813-43814 ( 2) 11886 UnlockIm sync Unsigned 4 0 - - Invisible
43815-43822 ( 8) 11882 Unlock Me String0 16 - - - Comms settings
43823-43830 ( 8) 11883 (N/A)
43831 11884 (N/A)
43832 11885 (N/A)
43833 11719 WatchedContr Unsigned 1 0 0 16 ProcessControl
43834 11866 (N/A)
43835 11867 kWhours dec Integer 1 0 -128 127 Statistics
43836 11868 kVArhours dec Integer 1 0 -128 127 Statistics
43837 12439 Derating2 mid x Integer 2 0 10189* 10190* ProcessControl
43838 12440 Derate2MidPwr % Unsigned 2 0 10191* 100 ProcessControl
43839 13573 SteppCtrlType List#39 1 - 1238 1240 IO TEDOM
43840 13574 SteppOpenTime s Unsigned 2 2 1 6000 IO TEDOM
43841 13575 SteppOpenSteps st Unsigned 2 0 1 10000 IO TEDOM
43842 13576 SteppSpeedMax st/s Unsigned 2 0 25 6000 IO TEDOM
43843 13577 SteppSpeedStrt st/s Unsigned 2 0 25 6000 IO TEDOM
43844 13578 SteppSpeedCal1 st/s Unsigned 2 0 25 6000 IO TEDOM
43845 13579 SteppSpeedCal2 st/s Unsigned 2 0 25 6000 IO TEDOM
43846 13581 SteppStartStps st Unsigned 2 0 0 6000 IO TEDOM
43847 13582 SteppPosToler st Unsigned 1 0 0 0 IO TEDOM
43848 13583 SteppPosHyst st Unsigned 1 0 0 0 IO TEDOM
43849 13584 SteppNomCurr % Unsigned 1 0 0 100 IO TEDOM
43850 13580 SteppCalType List#40 1 - 1241 1247 IO TEDOM
43851 12796 CrnkSeq pause min Unsigned 2 0 1 60 Engine params
43852-43853 ( 2) 12923 (N/A)
43854 12954 LastUser1 Unsigned 2 0 0 65535 Statistics
43855 12955 LastUser2 Unsigned 2 0 0 65535 Statistics
43856 12956 LastUser3 Unsigned 2 0 0 65535 Statistics
43857-43858 ( 2) 12957 LastUser1Date Date 3 - - - Statistics
43859-43860 ( 2) 12958 LastUser2Date Date 3 - - - Statistics
43861-43862 ( 2) 12959 LastUser3Date Date 3 - - - Statistics
43863-43864 ( 2) 12960 LastUser1Time Time 3 - - - Statistics
43865-43866 ( 2) 12961 LastUser2Time Time 3 - - - Statistics
43867-43868 ( 2) 12962 LastUser3Time Time 3 - - - Statistics
43869 12963 (N/A)
43870 12486 ExcitationLoss % Integer 2 0 0 150 Gener protect
43871 12487 ExctLoss del s Unsigned 2 1 0 6000 Gener protect
43872 13223 Peak kVA Start kVA Integer 2 1 13224* 32000 ProcessControl
43873 13224 Peak kVA Stop kVA Integer 2 1 0 13223* ProcessControl
43874 13225 PeakKVAS/S del s Unsigned 2 0 0 3200 ProcessControl
43875-43890 (16) 13276 AcallCH4-Addr String0 32 - - - Act. calls/SMS
43891-43906 (16) 13277 AcallCH5-Addr String0 32 - - - Act. calls/SMS
43907 13274 AcallCH4-Type List#30 1 - 1112 1120 Act. calls/SMS
43908 13275 AcallCH5-Type List#30 1 - 1112 1120 Act. calls/SMS
43909 13290 Nom EthFltCurr A Unsigned 2 0 0 10000 Gener protect
43910 13291 2EthFltCur del s Unsigned 2 1 0 6000 Gener protect
43911 8564 (N/A)
43912 8607 ReqWaterT °C Integer 2 1 0 1200 CHP Control
43913 8608 WaterTtoler °C Unsigned 2 1 0 1200 CHP Control
43914 8610 WaterTperiod s Unsigned 2 1 1 100 CHP Control
43915 13534 Gain % Integer 2 1 0 2000 CHP Control
43916 13535 Integer % Integer 2 0 0 100 CHP Control
43917 8609 OpenTime3WayV s Unsigned 2 1 1 10000 CHP Control
43918 8620 MaxTLim °C Integer 2 1 0 1200 CHP Control
43919 13568 MaxTLimHyst °C Integer 2 1 0 1200 CHP Control
43920 8621 TRiseLim °C Integer 2 1 0 1200 CHP Control
43921 13569 StartTRiseLim °C Integer 2 1 0 1200 CHP Control
43922 8688 Cooler On °C Integer 2 0 8689* 150 CHP Control
43923 8689 Cooler Off °C Integer 2 0 0 8688* CHP Control
43924 12986 RestPos 3wayV List#41 1 - 1110 1111 CHP Control
43925 10686 Suspension T °C Integer 2 1 10687* 1200 CHP Control
43926 10687 Resume T °C Integer 2 1 0 10686* CHP Control
43927 11537 OilFillOn s Unsigned 2 0 0 30 Engine params
43928 11538 OilFillPause min Unsigned 2 0 1 240 Engine params
43929 11541 OilFillDel s Unsigned 2 0 0 11537* Engine params
43930 13907 (N/A)
43931 13908 (N/A)
43932 13143 LAM filtr Unsigned 1 0 0 100 AFS control
43933 14020 (N/A)
43934 14352 LamVoltTolerA mV Integer 2 0 0 1200 AFS control
43935 14353 LamVoltTolerB mV Integer 2 0 0 1200 AFS control
43936 14354 TAFSOFFA s Unsigned 1 0 0 30 AFS control
43937 14355 TAFSOFFB s Unsigned 1 0 0 30 AFS control
43938 14356 TAFSERRA s Unsigned 2 0 0 300 AFS control
43939 14357 TAFSERRB s Unsigned 2 0 0 300 AFS control
43940 14358 StartTimeAFSA s Unsigned 2 0 0 600 AFS control
43941 14359 StartTimeAFSB s Unsigned 2 0 0 600 AFS control
43942 10068 Ana CH4A List#42 1 - 1136 1138 AFS control
43943 10790 MxPos40%CH4A % Unsigned 2 2 0 10000 AFS control
43944 10791 MxPos60%CH4A % Unsigned 2 2 0 10000 AFS control
43945 14360 MxPos40%CH4B % Unsigned 2 2 0 10000 AFS control
43946 14361 MxPos60%CH4B % Unsigned 2 2 0 10000 AFS control
43947 14362 Ana CH4B List#43 1 - 1139 1141 AFS control
43948 10064 StartPositionB % Unsigned 2 2 0 10000 AFS control
43949 10066 RunPositionB % Unsigned 2 2 0 10000 AFS control
43950 11575 LoPwrPositionB % Unsigned 2 2 0 10000 AFS control
43951 8456 LAM power 1B kW Integer 2 1 0 8457* AFS control
43952 8457 LAM power 2B kW Integer 2 1 8456* 8458* AFS control
43953 8458 LAM power 3B kW Integer 2 1 8457* 8459* AFS control
43954 8459 LAM power 4B kW Integer 2 1 8458* 8460* AFS control
43955 8460 LAM power 5B kW Integer 2 1 8459* 32000 AFS control
43956 8468 LAM 1B mV Integer 2 0 1 1200 AFS control
43957 8469 LAM 2B mV Integer 2 0 1 1200 AFS control
43958 8470 LAM 3B mV Integer 2 0 0 1200 AFS control
43959 8471 LAM 4B mV Integer 2 0 0 1200 AFS control
43960 8472 LAM 5B mV Integer 2 0 0 1200 AFS control
43961 8742 MixPos 1B % Integer 2 2 0 10000 AFS control
43962 8743 MixPos 2B % Integer 2 2 0 10000 AFS control
43963 8744 MixPos 3B % Integer 2 2 0 10000 AFS control
43964 8745 MixPos 4B % Integer 2 2 0 10000 AFS control
43965 8746 MixPos 5B % Integer 2 2 0 10000 AFS control
43966 12894 Sync attempts Unsigned 1 0 1 10 Sync/Load ctrl

* - limit is defined by the value of the communication object of specified number

============================================================================================
Register Protection#2 Protection#1
============================================================================================
45751 Smoke Detect C Ext Start/Stop
45752 Emergency Stop Status GCB
45753 GenOver-Curr Fuel Pres Low
45754 Leakage Low Press Oil
45755 LowLevel Oil RES-BB-BI10
45756 RES-BB-BI11 RES-BB-BI12
45757 RES-BB-BI13 RES-BB-BI14
45758 RES-BB-BI15 Status MCB
45759 RES-PTM1BI1 RES-PTM1BI2
45760 RES-PTM1BI3 RES-PTM1BI4
45761 RES-PTM1BI5 RES-PTM1BI6
45762 RES-PTM1BI7 RES-PTM1BI8
45763 N/A N/A
45764 N/A N/A
45765 N/A N/A
45766 N/A N/A
45767 N/A N/A
45768 N/A N/A
45769 N/A N/A
45770 N/A N/A
45771 N/A N/A
45772 N/A N/A
45773 N/A N/A
45774 N/A N/A
45775 N/A N/A
45776 N/A N/A
45777 N/A N/A
45778 N/A N/A
45779 N/A N/A
45780 N/A N/A
45781 N/A N/A
45782 N/A N/A
45783 SuspendT VPIO-1 2
45784 VPIO-1 3 VPIO-1 4
45785 VPIO-1 5 VPIO-1 6
45786 VPIO-1 7 VPIO-1 8
45787 N/A N/A
45788 N/A N/A
45789 N/A N/A
45790 N/A N/A
45791 N/A N/A
45792 N/A N/A
45793 N/A N/A
45794 N/A N/A
45795 N/A N/A
45796 N/A N/A
45797 N/A N/A
45798 N/A N/A
45799 N/A N/A
45800 N/A N/A
45801 N/A N/A
45802 N/A N/A
45803 N/A N/A
45804 N/A N/A
45805 N/A N/A
45806 N/A N/A
45807 N/A N/A
45808 N/A N/A
45809 N/A N/A
45810 N/A N/A
45811 N/A N/A
45812 N/A N/A
45813 N/A N/A
45814 N/A N/A
45815 N/A N/A
45816 N/A N/A
45817 N/A N/A
45818 N/A N/A
45819 N/A N/A
45820 N/A N/A
45821 N/A N/A
45822 N/A N/A
45823 CKPS-0 CPMS-0
45824 CanSetEnable-0 Firing-0
45825 Selftest-0 ECU Comm OK-0
45826 AmberWrnLamp-0 RedStopLamp-0
45827 CKPS-1 CPMS-1
45828 CanSetEnable-1 Firing-1
45829 Selftest-1 ECU Comm OK-1
45830 AmberWrnLamp-1 RedStopLamp-1
45831 N/A N/A
45832 N/A N/A
45833 N/A N/A
45834 N/A N/A
45835 N/A N/A
45836 N/A N/A
45837 N/A N/A
45838 N/A N/A
45839 N/A N/A
45840 N/A N/A
45841 N/A N/A
45842 N/A N/A
45843 N/A N/A
45844 N/A N/A
45845 N/A N/A
45846 N/A N/A
45847 WaterLevel Command
45848 CalibrActive CalibrSuccess
45849 ErrCalTimeOut ErrBothSens
45850 ErrOverCurr EndPosLost
45851 Reserved ErrCalibrFail
45852 WrongParams Reserved
45853 CommonErr Increasing
45854 Decreasing Reserved
45855 MixRichClapPos T Canopy
45856 Oil Temperat Press Oil
45857 T P.C. In T P.C. Out
45858 T S.C. Gen T S.C. In
45859 N/A N/A
45860 N/A N/A
45861 N/A N/A
45862 N/A N/A
45863 N/A N/A
45864 N/A N/A
45865 N/A N/A
45866 N/A N/A
45867 N/A N/A
45868 N/A N/A
45869 N/A N/A
45870 N/A N/A
45871 N/A N/A
45872 N/A N/A
45873 N/A N/A
45874 N/A N/A
45875 N/A N/A
45876 N/A N/A
45877 Engine Speed-0 GlobalTiming-0
45878 Timing1-0 Timing2-0
45879 Timing3-0 Timing4-0
45880 Dwell time 1-0 Dwell time 2-0
45881 Dwell time 3-0 Dwell time 4-0
45882 Dwell optim1-0 Dwell optim2-0
45883 Dwell optim3-0 Dwell optim4-0
45884 Battery Volt-0 Engine Speed-1
45885 N/A N/A
45886 N/A N/A
45887 N/A N/A
45888 N/A N/A
45889 N/A N/A
45890 N/A N/A
45891 N/A N/A
45892 N/A N/A
45893 N/A N/A
45894 T S.C. Out Reserve
45895 T.Cat Reserve
45896 Lambda S Lambda L
45897 BuildConsumpt StepperPos
45898 IGS-PTM(1) BIN BIN 2
45899 BIN 3 BIN 4
45900 BIN 5 BIN 6
45901 IGS-PTM(1) AIN ANA 2
45902 ANA 3 ANA 4
45903 IGS-PTM(1)BOUT BOUT 2
45904 BOUT 3 BOUT 4
45905 BOUT 5 BOUT 6
45906 IGS-PTM(1)AOUT AOUT 2
45907 AOUT 3 AOUT 4
45908 ECU SHBIN 1
45909 SHBIN 2 SHBIN 3
45910 SHBIN 4 SHBIN 5
45911 SHBIN 6 SHAIN 1
45912 SHAIN 2 SHBinCfgErr
45913 SHAinCfgErr ECON4
45914 IO TEDOM PumpsManActive
45915 ClapManActive MF Ret Bypass
45916 Failure net ActCall Fail
45917 ECUDiagBlocked Wrong config
45918 RTCbatteryFlat System error
45919 UnauthorizCopy Batt volt
45920 Gen V unbal Gen I unbal
45921 RedPWR A+H Gen I unbal
45922 Al/Hist.msg 6 Al/Hist.msg 7
45923 Al/Hist.msg 8 Al/Hist.msg 9
45924 Al/Hist.msg 10 Al/Hist.msg 11
45925 Al/Hist.msg 12 Al/Hist.msg 13
45926 Al/Hist.msg 14 Al/Hist.msg 15
45927 Al/Hist.msg 16 Dongle incomp
45928 Emergency stop RPM
45929 CAN2 bus empty Stop fail
45930 Overspeed Underspeed
45931 Pickup fail Sd ExtBattFlat
45932 WrnServiceT1+2 WrnServiceT3
45933 Sd ServiceTime Not lubricated
45934 Start fail Start blocking
45935 Wrn CylTemp1 Wrn CylTemp2
45936 Wrn CylTemp3 Wrn CylTemp4
45937 Wrn CylTemp5 Wrn CylTemp6
45938 Wrn CylTemp7 Wrn CylTemp8
45939 Wrn MCB fail Stp GCB fail
45940 Sd Oil press B Wrn RSync fail
45941 Stp Sync fail BOC L1 under
45942 BOC L2 under BOC L3 under
45943 BOC L1 over BOC L2 over
45944 BOC L3 over Sd L1 over
45945 Sd L2 over Sd L3 over
45946 BOC L12 under BOC L23 under
45947 BOC L31 under BOC L12 over
45948 BOC L23 over BOC L31 over
45949 Sd L12 over Sd L23 over
45950 Sd L31 over Gen V L1-N
45951 Gen V L2-N Gen V L3-N
45952 Gen V L1-L2 Gen V L2-L3
45953 Gen V L3-L1 Gen freq
45954 BOC fgen under BOC fgen over
45955 BOC ReversePwr MP L1 under 1
45956 MP L2 under 1 MP L3 under 1
45957 MP L1 over 1 MP L2 over 1
45958 MP L3 over 1 MP L1 under 2
45959 MP L2 under 2 MP L3 under 2
45960 MP L1 over 2 MP L2 over 2
45961 MP L3 over 2 MP L12 under 1
45962 MP L23 under 1 MP L31 under 1
45963 MP L12 over 1 MP L23 over 1
45964 MP L31 over 1 MP L12 under 2
45965 MP L23 under 2 MP L31 under 2
45966 MP L12 over 2 MP L23 over 2
45967 MP L31 over 2 MP fmns under1
45968 MP fmns over1 MP fmns under2
45969 MP fmns over2 Mains V L1-N
45970 Mains V L2-N Mains V L3-N
45971 Mains V L1-L2 Mains V L2-L3
45972 Mains V L3-L1 Mains freq
45973 Mains V unbal Bus meas error
45974 OfL StartBlck BOC IDMT
45975 BOC ShortCurr BOC Overload
45976 BOC NCB fail Wrn BadPwrCfg
45977 Wrn Addr error Manual Restore
45978 WrnTstOnLdFail Wrn SpdRegLim
45979 Wrn VoltRegLim G L neg
45980 G ph+L neg G ph opposed
45981 M L neg M ph+L neg
45982 M ph opposed PassInsertBlck
45983 Sd GasVTest UsDngl Expired
45984 UsDngl NoAcces UsDngl Incompa
45985 Cleaning BOC ExctLoss
45986 BOC Ieth IDMT Incom. periph.
45987 BO 1 BO 2
45988 BO 3 BO 4
45989 BO 5 BO 6
45990 BO 7 BO 8
45991 BO 9 BO 10
45992 BO 11 BO 12
45993 DISTBIN 01 DISTBIN 02
45994 DISTBIN 03 DISTBIN 04
45995 DISTBIN 05 DISTBIN 06
45996 DISTBIN 07 DISTBIN 08
45997 DISTBIN 09 DISTBIN 10
45998 DISTBIN 11 DISTBIN 12
45999 DISTBIN 13 DISTBIN 14
46000 DISTBIN 15 DISTBIN 16
46201 DISTBIN 17 DISTBIN 18
46202 DISTBIN 19 DISTBIN 20
46203 DISTBIN 21 DISTBIN 22
46204 DISTBIN 23 DISTBIN 24
46205 DISTBIN 25 DISTBIN 26
46206 DISTBIN 27 DISTBIN 28
46207 DISTBIN 29 DISTBIN 30
46208 DISTBIN 31 DISTBIN 32
46209 GenPwrCtrlFail Mains fail
46210 OilFillPumpErr N/A
46211 N/A N/A
46212 N/A N/A
46213 N/A N/A
46214 N/A N/A
46215 N/A N/A
46216 N/A N/A
46217 N/A N/A
46218 N/A N/A
46219 N/A N/A
46220 N/A N/A
46221 N/A N/A
46222 N/A N/A
46223 N/A N/A
46224 N/A N/A
46225 N/A N/A
46226 N/A N/A
46227 N/A N/A
46228 N/A N/A
46229 N/A N/A
46230 N/A N/A
46231 N/A N/A
46232 N/A N/A
46233 N/A N/A
46234 N/A N/A
46235 N/A N/A
46236 N/A N/A
46237 N/A N/A
46238 N/A N/A
46239 N/A N/A
46240 N/A N/A
46241 N/A N/A
46242 N/A N/A
46243 N/A N/A
46244 N/A N/A
46245 N/A N/A
46246 N/A N/A
46247 N/A N/A
46248 N/A N/A
46249 N/A N/A
46250 N/A N/A
46251 N/A N/A
46252 N/A N/A
46253 N/A N/A
46254 N/A N/A
46255 N/A N/A
46256 N/A N/A
46257 N/A N/A
46258 N/A N/A
46259 N/A N/A
46260 N/A N/A
46261 N/A N/A
46262 N/A N/A
46263 N/A N/A
46264 N/A N/A
46265 N/A N/A
46266 N/A N/A
46267 N/A N/A
46268 N/A N/A
46269 N/A N/A
46270 N/A N/A
46271 N/A N/A
46272 N/A N/A
46273 N/A N/A
46274 N/A N/A
46275 N/A N/A
46276 N/A N/A
46277 N/A N/A
46278 N/A N/A
46279 N/A N/A
46280 N/A N/A
46281 N/A N/A
46282 N/A N/A
46283 N/A N/A
46284 N/A N/A
46285 N/A N/A
46286 N/A N/A
46287 N/A N/A
46288 N/A N/A
46289 N/A N/A
46290 N/A N/A
46291 N/A N/A
46292 N/A N/A
46293 N/A N/A
46294 N/A N/A
46295 N/A N/A
46296 N/A N/A
46297 N/A N/A
46298 N/A N/A
46299 N/A N/A
46300 N/A N/A
46301 N/A N/A
46302 N/A N/A
46303 N/A N/A
46304 N/A N/A
46305 N/A N/A
46306 N/A N/A
46307 N/A N/A
46308 N/A N/A
46309 N/A N/A
46310 N/A N/A
46311 N/A N/A
46312 N/A N/A
46313 N/A N/A
46314 N/A N/A
46315 N/A N/A
46316 N/A N/A
46317 N/A N/A
46318 N/A N/A
46319 N/A N/A
46320 N/A N/A
46321 N/A N/A
46322 N/A N/A
46323 N/A N/A
46324 N/A N/A
46325 N/A N/A

Protections
------------------------------------------------------------------

Register map:
Bit 0-7 ................. Protection #1
Bit 8-15 ............... Protection #2

Bit 0-2 ................. Protection #1 Level 1
Value Meaning
------------------------------------------------------------------
0 Level 1 inactive
1 N/A
2 Level 1 active, confirmed
3 Level 1 active, but blocked or delay still running
4 Level 1 previously active, not confirmed yet
5 N/A
6 Level 1 active, not confirmed yet
7 Level 1 active, not confirmed yet, blocked

Bit 3-5 ................. Protection #1 Level 2
Value Meaning
------------------------------------------------------------------
0 Level 2 inactive
1 N/A
2 Level 2 active, confirmed
3 Level 2 active, but blocked or delay still running
4 Level 2 previously active, not confirmed yet
5 N/A
6 Level 2 active, not confirmed yet
7 Level 2 active, not confirmed yet, blocked

Bit 6-7 ................. Protection #1 Sensor failure
Value Meaning
------------------------------------------------------------------
0 Sensor failure not active
1 Sensor failure active, confirmed
2 Sensor failure previously active, not confirmed yet
3 Sensor failure active, not confirmed yet

Bit 8-10 ................. Protection #2 Level 1
Value Meaning
------------------------------------------------------------------
0 Level 1 inactive
1 N/A
2 Level 1 active, confirmed
3 Level 1 active, but blocked or delay still running
4 Level 1 previously active, not confirmed yet
5 N/A
6 Level 1 active, not confirmed yet
7 Level 1 active, not confirmed yet, blocked

Bit 11-13 ................. Protection #2 Level 2
Value Meaning
------------------------------------------------------------------
0 Level 2 inactive
1 N/A
2 Level 2 active, confirmed
3 Level 2 active, but blocked or delay still running
4 Level 2 previously active, not confirmed yet
5 N/A
6 Level 2 active, not confirmed yet
7 Level 2 active, not confirmed yet, blocked

Bit 14-15 ................. Protection #2 Sensor failure
Value Meaning
------------------------------------------------------------------
0 Sensor failure not active
1 Sensor failure active, confirmed (or not configured as protection)
2 Sensor failure previously active, not confirmed yet
3 Sensor failure active, not confirmed yet

----------------------------------------------------------------------------------

======================================================================================
List# Types Meaning
======================================================================================

--------------------------------------------------------------------------------------
List#1

Value Name
--------------------------------------------------------------------------------------
    0 ECU-StrList1

--------------------------------------------------------------------------------------
List#2

Value Name
--------------------------------------------------------------------------------------
    0 ECU-StrList2

--------------------------------------------------------------------------------------
List#3

Value Name
--------------------------------------------------------------------------------------
    0 Init
    1 Ready
    2 NotReady
    3 Prestart
    4 Cranking
    5 Pause
    6 Starting
    7 Running
    8 Loaded
    9 Soft unld
   10 Cooling
   11 Stop
   12 Shutdown
   13 Ventil
   14 EmergMan
   15 Cooldown
   16 Offload
   17 Soft load
   18 WaitStop
   19 Warming
   20 SDVentil
   21 GasVTest

--------------------------------------------------------------------------------------
List#4

Value Name
--------------------------------------------------------------------------------------
    0 Init
    1 BrksOff
    2 IslOper
    3 MainsOper
    4 ParalOper
    5 RevSync
    6 Synchro
    7 MainsFlt
    8 ValidFlt
    9 MainsRet
   10 MultIslOp
   11 MultParOp
   12 EmergMan

--------------------------------------------------------------------------------------
List#5

Value Name
--------------------------------------------------------------------------------------
    0 OFF
    1 MAN
    2 SEM
    3 AUT
    4 TEST

--------------------------------------------------------------------------------------
List#6

Value Name
--------------------------------------------------------------------------------------
    0 No Timer
    1 Prestart
    2 Cranking
    3 Idle run
    4 Cooling
    5 Stop time
    6 AfterCool
    7 Pause
    8 MinStabTO
    9 MaxStabTO
   10 Wait stop
   11 Warming
   12 MCB close
   13 FwRet brk
   14 SyncTOut
   15 BrkOvrlap
   16 GCB open
   17 SyncStart
   18 RetTransf
   19 ValidFlt
   20 Soft load
   21 Soft unld
   22 VentilGas
   23 SystStart
   24 SystStop
   25 NextStart
   26 NextStop
   27 LdShedChg
   28 LdRecChg
   29 SyncEnab
   30 OfL stop
   31 GasVTest
   32 StartBlockDel

--------------------------------------------------------------------------------------
List#7

Value Name
--------------------------------------------------------------------------------------
    0 NONE
    1 J1939-DM1
    2 J1939-KWP
    3 J1587-DTC
    4 MODBUS

--------------------------------------------------------------------------------------
List#8

Value Name
--------------------------------------------------------------------------------------
    0 No LoadShed
    1 LdShed S1
    2 LdShed S2
    3 LdShed S3

--------------------------------------------------------------------------------------
List#9

Value Name
--------------------------------------------------------------------------------------
    0 None
    1 Island
    2 BaseLd
    3 BLdExLm
    4 PwrI/E
    5 TbyPwr

--------------------------------------------------------------------------------------
List#10

Value Name
--------------------------------------------------------------------------------------
    0 None
    1 Island
    2 BasePF
    3 PF I/E

--------------------------------------------------------------------------------------
List#11

Value Name
--------------------------------------------------------------------------------------
    0 RET
    1 ADV

--------------------------------------------------------------------------------------
List#12

Value Name
--------------------------------------------------------------------------------------
    0 ATDC
    1 BTDC

--------------------------------------------------------------------------------------
List#13

Value Name
--------------------------------------------------------------------------------------
    0 /5A
    1 /1A

--------------------------------------------------------------------------------------
List#14

Value Name
--------------------------------------------------------------------------------------
    0 277 V
    1 120 V

--------------------------------------------------------------------------------------
List#15

Value Name
--------------------------------------------------------------------------------------
    0 PHASE-NEUTRAL
    1 PHASE-PHASE

--------------------------------------------------------------------------------------
List#16

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 ENABLED

--------------------------------------------------------------------------------------
List#17

Value Name
--------------------------------------------------------------------------------------
    0 PANEL
    1 EXTBUTTONS
    2 BOTH

--------------------------------------------------------------------------------------
List#18

Value Name
--------------------------------------------------------------------------------------
    0 IDLE
    1 NOMINAL

--------------------------------------------------------------------------------------
List#19

Value Name
--------------------------------------------------------------------------------------
    0 BASELOAD
    1 IM/EX
    2 ANEXT BASELOAD
    3 ANEXT IM/EX
    4 T BY PWR

--------------------------------------------------------------------------------------
List#20

Value Name
--------------------------------------------------------------------------------------
    0 BASEPF
    1 PF-IM/EX
    2 ANEXT BASEPF
    3 ANEXT PF-IM/EX

--------------------------------------------------------------------------------------
List#21

Value Name
--------------------------------------------------------------------------------------
    0 NONE
    1 IM3 CT INPUT
    2 ANALOG INPUT

--------------------------------------------------------------------------------------
List#22

Value Name
--------------------------------------------------------------------------------------
    0 NO
    1 YES

--------------------------------------------------------------------------------------
List#23

Value Name
--------------------------------------------------------------------------------------
    0 NONE
    1 FORWARD
    2 REVERSE
    3 BOTH

--------------------------------------------------------------------------------------
List#24

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 PARALLEL ONLY
    2 ENABLED

--------------------------------------------------------------------------------------
List#25

Value Name
--------------------------------------------------------------------------------------
    0 MCB
    1 GCB

--------------------------------------------------------------------------------------
List#26

Value Name
--------------------------------------------------------------------------------------
    0 MAINSFAIL
    1 GEN RUNNING

--------------------------------------------------------------------------------------
List#27

Value Name
--------------------------------------------------------------------------------------
    0 MANUAL
    1 AUTO

--------------------------------------------------------------------------------------
List#28

Value Name
--------------------------------------------------------------------------------------
    0 POSITIVE
    1 NEGATIVE

--------------------------------------------------------------------------------------
List#29

Value Name
--------------------------------------------------------------------------------------
    0 ALL THE TIME
    1 SYNC ONLY

--------------------------------------------------------------------------------------
List#30

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 DATA-ANA
    2 DATA-GSM
    3 DATA-ISDN
    4 DATA-CDMA
    5 SMS-GSM
    6 SMS-CDMA
    7 IB-E-MAIL
    8 IB-EML-SMS

--------------------------------------------------------------------------------------
List#31

Value Name
--------------------------------------------------------------------------------------
    0 OFF
    1 ON

--------------------------------------------------------------------------------------
List#32

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 ENGINE RUNNING
    2 ALWAYS

--------------------------------------------------------------------------------------
List#33

Value Name
--------------------------------------------------------------------------------------
    0 EACH
    1 COMMON

--------------------------------------------------------------------------------------
List#34

Value Name
--------------------------------------------------------------------------------------
    0 STOP
    1 INFIN COOLING

--------------------------------------------------------------------------------------
List#35

Value Name
--------------------------------------------------------------------------------------
    0 DISABLE
    1 ISLAND ONLY
    2 ISL+TRIP PARAL
    3 ALL THE TIME

--------------------------------------------------------------------------------------
Timer-L#36

Value Name
--------------------------------------------------------------------------------------
    0 OFF
    1 ONCE
    2 DAILY
    3 WEEKLY
    4 MONTHLY
    5 MONTHLY
    6 PERIOD
    7 N/A

Timer Type Meaning

Common part (in all modes):
  Bits 0- 6: Year (offset from 2000 => 2000-2127)
  Bits 7-10: Month (1-12)
  Bits 11-15: Day (1-31)
  Bits 16-31: Time (number of minutes from midnight => 0-1439)
    Year,Month,Day,Time = first start of timer (N/A in OFF mode)
  Bits 32-44: Duration (in minutes => 1-1439) (N/A in OFF mode)
  Bits 45-47: Mode
    0 = OFF
    1 = Once
    2 = Daily
    3 = Weekly
    4 = Monthly
    5 = Monthly (in day of week)
    6 = Period
    7 = N/A (OFF)

In OFF, Once, N/A mode:
  Bits 48-63: N/A

In Daily Mode:
  Bits 48-57: Repeat period (in days => 1-1023)
  Bits 58-59: Weekend mode:
    0 = including weekend days
    1 = except weekend days
    2 = postpone weekend days (to Monday)
    3 = N/A
  Bits 60-63: N/A

In Weekly Mode:
  Bits 48-53: Repeat period (in weeks => 1-63)
  Bit 54: on Monday
  Bit 55: on Tuesday
  Bit 56: on Wednesday
  Bit 57: on Thursday
  Bit 58: on Friday
  Bit 59: on Saturday
  Bit 60: on Sunday
  Bits 61-63: N/A

In Monthly Mode:
  Bits 48-51: Repeat period (in months => 1-15)
  Bits 52-56: Number of day in month (1-31)
  Bits 57-63: N/A

In Monthly (in day of week) Mode:
  Bits 48-51: Repeat period (in months => 1-15)
  Bits 52-54: Number of week in month (1-5)
  Bits 55-56: N/A
  Bit 57: on Monday
  Bit 58: on Tuesday
  Bit 59: on Wednesday
  Bit 60: on Thursday
  Bit 61: on Friday
  Bit 62: on Saturday
  Bit 63: on Sunday
    Note: currently only one day of week can be selected.
    Please refer to manual.

In Period Mode:
  Bits 48-63: Repeat period (in minutes => 1-65535)

--------------------------------------------------------------------------------------
List#37

Value Name
--------------------------------------------------------------------------------------
    0 MANUAL
    1 AUTOMATIC

--------------------------------------------------------------------------------------
List#38

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 ENABLED

--------------------------------------------------------------------------------------
List#39

Value Name
--------------------------------------------------------------------------------------
    0 Up/Dn
    1 Analog
    2 Outputs

--------------------------------------------------------------------------------------
List#40

Value Name
--------------------------------------------------------------------------------------
    0 ProxSens0
    1 ProxSens100
    2 ProxSens0+100
    3 MechEnd0
    4 MechEnd100
    5 ProxSens+LimSw
    6 No calibration

--------------------------------------------------------------------------------------
List#41

Value Name
--------------------------------------------------------------------------------------
    0 UP
    1 DOWN

--------------------------------------------------------------------------------------
List#42

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 ENA-FIX
    2 ENA-STEP

--------------------------------------------------------------------------------------
List#43

Value Name
--------------------------------------------------------------------------------------
    0 DISABLED
    1 ENA-FIX
    2 ENA-STEP

======================================================================================
Binary# Types Meaning
======================================================================================

--------------------------------------------------------------------------------------
Binary#1

Bit Name
--------------------------------------------------------------------------------------
  0 Smoke Detect C
  1 Ext Start/Stop
  2 Emergency Stop
  3 Status GCB
  4 GenOver-Curr
  5 Fuel Pres Low
  6 Leakage
  7 Low Press Oil
  8 LowLevel Oil
  9 RES-BB-BI10
 10 RES-BB-BI11
 11 RES-BB-BI12
 12 RES-BB-BI13
 13 RES-BB-BI14
 14 RES-BB-BI15
 15 Status MCB

--------------------------------------------------------------------------------------
Binary#2

Bit Name
--------------------------------------------------------------------------------------
  0 RES-PTM1BI1
  1 RES-PTM1BI2
  2 RES-PTM1BI3
  3 RES-PTM1BI4
  4 RES-PTM1BI5
  5 RES-PTM1BI6
  6 RES-PTM1BI7
  7 RES-PTM1BI8

--------------------------------------------------------------------------------------
Binary#3

Bit Name
--------------------------------------------------------------------------------------
  0 Starter
  1 RPM Regulator
  2 FuelSolenoid 1
  3 GCB close/open
  4 Failure
  5 Engine Run BO
  6 Pumps Island
  7 Pumps Paralel
  8 Probe Heating
  9 Mains Fail
 10 Reg S.C.Servo+
 11 Reg S.C.Servo-
 12 FuelSolen Fail
 13 Common Wrn
 14 Gen Breaker MX
 15 MCB Blocking

--------------------------------------------------------------------------------------
Binary#4

Bit Name
--------------------------------------------------------------------------------------
  0 CKPS-0
  1 CPMS-0
  2 CanSetEnable-0
  3 Firing-0
  4 Selftest-0
  5 ECU Comm OK-0
  6 AmberWrnLamp-0
  7 RedStopLamp-0

--------------------------------------------------------------------------------------
Binary#5

Bit Name
--------------------------------------------------------------------------------------
  0 CKPS-1
  1 CPMS-1
  2 CanSetEnable-1
  3 Firing-1
  4 Selftest-1
  5 ECU Comm OK-1
  6 AmberWrnLamp-1
  7 RedStopLamp-1

--------------------------------------------------------------------------------------
Binary#6

Bit Name
--------------------------------------------------------------------------------------
  0 Ignition
  1 ECU-BOUT 2
  2 ECU-BOUT 3
  3 ECU-BOUT 4
  4 ECU-BOUT 5
  5 ECU-BOUT 6
  6 ECU-BOUT 7
  7 ECU-BOUT 8

--------------------------------------------------------------------------------------
Binary#7

Bit Name
--------------------------------------------------------------------------------------
  0 ECU-BOUT 9
  1 ECU-BOUT 10
  2 ECU-BOUT 11
  3 ECU-BOUT 12
  4 ECU-BOUT 13
  5 ECU-BOUT 14
  6 ECU-BOUT 15
  7 ECU-BOUT 16

--------------------------------------------------------------------------------------
Binary#8

Bit Name
--------------------------------------------------------------------------------------
  0 Starter
  1 Fuel solenoid
  2 FuelSolPulse
  3 Prestart
  4 Alarm
  5 Horn
  6 CommonAlLev 1
  7 CommonAlLev 2
  8 Cooling pump
  9 GCB close/open
 10 GCB ON coil
 11 GCB OFF coil
 12 GCB UV coil
 13 MCB close/open
 14 MCB ON coil
 15 MCB OFF coil

--------------------------------------------------------------------------------------
Binary#9

Bit Name
--------------------------------------------------------------------------------------
  0 MCB UV coil
  1 Stop solenoid
  2 Stop pulse
  3 Reserved
  4 Reserved
  5 Reserved
  6 Reserved
  7 Reserved
  8 Reserved
  9 Speed up
 10 Speed dn
 11 AVR up
 12 AVR dn
 13 kWh pulses
 14 CommActive
 15 WrongPhSeq

--------------------------------------------------------------------------------------
Binary#10

Bit Name
--------------------------------------------------------------------------------------
  0 Vgen <>
  1 Vmains <>
  2 Overcurrent
  3 VectorShiftTrp
  4 VectorShiftAct
  5 Common Wrn
  6 Common Sd
  7 Common SdOvr
  8 Common Stp
  9 Common Fls
 10 Common LOP
 11 Common OfL
 12 Common BOC
 13 Common MP
 14 Common Al
 15 Common Hst

--------------------------------------------------------------------------------------
Binary#11

Bit Name
--------------------------------------------------------------------------------------
  0 CommonActLev 1
  1 CommonActLev 2
  2 Alarm flashing
  3 Horn flashing
  4 T cyl differ
  5 Ignition
  6 Ventilation
  7 Idle/Nominal
  8 Prelubr pump
  9 FltResButnEcho
 10 HornButnEcho
 11 StartButnEcho
 12 StopButnEcho
 13 GCBButnEcho
 14 MCBButnEcho
 15 GCB status

--------------------------------------------------------------------------------------
Binary#12

Bit Name
--------------------------------------------------------------------------------------
  0 MCB status
  1 GenParams OK
  2 MainsParams OK
  3 Reserved
  4 Reserved
  5 In synchronism
  6 Reserved
  7 Derating 1 act
  8 Derating 2 act
  9 Reserved
 10 Neutral CB C/O
 11 ECU PwrRelay
 12 ECU comm error
 13 PeriphCommErr
 14 CtrlHeartBeat
 15 CtrlHBeat FD

--------------------------------------------------------------------------------------
Binary#13

Bit Name
--------------------------------------------------------------------------------------
  0 LdShed stage 1
  1 LdShed stage 2
  2 LdShed stage 3
  3 TimerAct 1-4
  4 TimerAct 5-8
  5 TimerAct 9-12
  6 TimerAct 13-16
  7 TimerActiveCom
  8 Off mode
  9 Man mode
 10 Sem mode
 11 Aut mode
 12 Test mode
 13 Reserved
 14 Ready for load
 15 Stand-by ready

--------------------------------------------------------------------------------------
Binary#14

Bit Name
--------------------------------------------------------------------------------------
  0 Gen-set active
  1 Operational
  2 Ready
  3 Not ready
  4 CrankProcedure
  5 Starting
  6 Idle run
  7 Running
  8 ForwardSynchro
  9 ReverseSynchro
 10 Warming
 11 Soft load
 12 Loaded
 13 Soft unld
 14 Cooling
 15 Stopping

--------------------------------------------------------------------------------------
Binary#15

Bit Name
--------------------------------------------------------------------------------------
  0 SuspendT
  1 VPIO-1 2
  2 VPIO-1 3
  3 VPIO-1 4
  4 VPIO-1 5
  5 VPIO-1 6
  6 VPIO-1 7
  7 VPIO-1 8

--------------------------------------------------------------------------------------
Binary#16

Bit Name
--------------------------------------------------------------------------------------
  0 RemoteControl1
  1 RemoteControl2
  2 RemoteControl3
  3 RemoteControl4
  4 RemoteControl5
  5 RemoteControl6
  6 RemoteControl7
  7 RemoteControl8
--------------------------------------------------------------------------------------
Binary#17

Bit Name
--------------------------------------------------------------------------------------
  0 Ready
  1 Running
  2 Loaded
  3 Reserved
  4 SoftLoad
  5 Reserved
  6 SoftUnload
  7 Reserved
  8 WaitStop
  9 GenParams OK
 10 Warming
--------------------------------------------------------------------------------------
Binary#18

Bit Name
--------------------------------------------------------------------------------------
  0 MFprotec
  1 Engine Run BO
  2 Pumps Paral
  3 Del MFprotec
  4 GCB fdb del
  5 DelFuelSolen
  6 RPM Comp
  7 FuelSolen Fail

--------------------------------------------------------------------------------------
Binary#19

Bit Name
--------------------------------------------------------------------------------------
  0 GCB command de
  1 Gen Breaker MX
  2 Mains Fault
  3 MF Ret Bypass
  4 PLC-BOUT 2.5
  5 Parallel Off
  6 PLC-BOUT 2.7
  7 PLC-BOUT 2.8

--------------------------------------------------------------------------------------
Binary#20

Bit Name
--------------------------------------------------------------------------------------
  0 PLC-BOUT 3.1
  1 PMcmd1
  2 PMcmd2
  3 PumpsManual
  4 PMorCoolinPump
  5 PM only
  6 Pumps Paralel
  7 MixRichClapPow

--------------------------------------------------------------------------------------
Binary#21

Bit Name
--------------------------------------------------------------------------------------
  0 CM cmd1
  1 CM cmd2
  2 ClapManual
  3 Clap Manual
  4 Pumps Island
  5 PLC-BOUT 4.6
  6 PLC-BOUT 4.7
  7 PLC-BOUT 4.8

--------------------------------------------------------------------------------------
Binary#22

Bit Name
--------------------------------------------------------------------------------------
  0 MixRichClapPow
  1 RES-PTM1BO2
  2 RES-PTM1BO3
  3 RES-PTM1BO4
  4 RES-PTM1BO5
  5 RES-PTM1BO6
  6 RES-PTM1BO7
  7 RES-PTM1BO8

--------------------------------------------------------------------------------------
Binary#23

Bit Name
--------------------------------------------------------------------------------------
  0 Cranking
  1 Logical 0
  2 Logical 1
  3 Bin selector 1
  4 Bin selector 2
  5 Bin selector 3
  6 Bin selector 4
  7 AFS lim
  8 GasVTest run
  9 OilFiling pump
 10 Reserved
 11 User Button 1
 12 User Button 2
 13 User Button 3
 14 User Button 4
 15 User Button 5

--------------------------------------------------------------------------------------
Binary#24

Bit Name
--------------------------------------------------------------------------------------
  0 ActAlLev1
  1 ActAlLev2
  2 NotConfirmLev1
  3 NotConfirmLev2
  4 Reserved
  5 Not ready
  6 Ready
  7 Running
  8 Loaded
  9 MCB used
 10 MCB closed
 11 MCB synchro
 12 GCB used
 13 GCB closed
 14 GCB synchro
--------------------------------------------------------------------------------------
Binary#25

Bit Name
--------------------------------------------------------------------------------------
  0 User Button 6
  1 User Button 7
  2 User Button 8
  3 User Button 9
  4 User Button 10
  5 User Button 11
  6 User Button 12
  7 User Button 13
  8 User Button 14
  9 User Button 15
 10 User Button 16
 11 PeakShaveAct
 12 Reserved
 13 ThreewayLlvUp
 14 ThreewayLlvDn
 15 HeatingPump

--------------------------------------------------------------------------------------
Binary#26

Bit Name
--------------------------------------------------------------------------------------
  0 MaxTLim
  1 LimTRate
  2 SuspendT
  3 Cooler
  4 Power 1
  5 Power 2
  6 Power 3
  7 Power 4
  8 Power 5
  9 Gas A
 10 Gas B
 11 AFS Error
 12 Reserved
 13 Reserved
 14 Reserved
 15 Reserved

--------------------------------------------------------------------------------------
Binary#27

Bit Name
--------------------------------------------------------------------------------------
  0 K4 1
  1 K4 2
  2 K4 3
  3 K4 4
  4 K3 1
  5 K3 2
  6 K3 3
  7 K3 4

--------------------------------------------------------------------------------------
Binary#28

Bit Name
--------------------------------------------------------------------------------------
  0 FaultReset
  1 Calibration
  2 StepperEnable
  3 Up
  4 Down
  5 EndPos0
  6 EndPos100
  7 Reserved

--------------------------------------------------------------------------------------
Binary#29

Bit Name
--------------------------------------------------------------------------------------
  0 WaterLevel
  1 Command
  2 CalibrActive
  3 CalibrSuccess
  4 ErrCalTimeOut
  5 ErrBothSens
  6 ErrOverCurr
  7 EndPosLost
  8 Reserved
  9 ErrCalibrFail
 10 WrongParams
 11 Reserved
 12 CommonErr
 13 Increasing
 14 Decreasing
 15 Reserved

======================================================================================
Table# Types Meaning
======================================================================================